## Datasheet
PUMP DATA SHEET
| Model | MHI402I | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 100 | ℓ/min (Ht=20m 일때) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 20 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 20 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 55 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 750 | W | Impeller | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Shaft | STS316L
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | STS304
16 | Bore | Size(Dia) | Rating | Face | Position | Stage Housing | STS304
17 | Suction | 32mm |  | □ FF, □ RF | ■End □Top □Side | Shaft Sleeve | STS304
18 | Discharge | 25mm |  | □ FF, □ RF | ■Top, □Side
19 | Impeller Type | CLOSED | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6302ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 750W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type | MG1/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Multistage Horizontal Pump
MODEL |  | MHI402I
SERVICE
SCALE:N/S
OUTLINE DRAWING
of MHI TYPE

## Sectional
Sheet No.
CUSTOMER
ITEM No.
DATE
No. | Part name |  | Material |  | Q'NTY
|  |  | MHi00000 | MHi00000S
0000 | MOTOR |  | - |  | 1
1111 | CASING |  | STS304 | STS316L | 1
1150 | STAGE HOUSING |  | STS304 | STS316L | n-1
1154 | STAGE CENTERING |  | STS304 | STS316L | 1
1160 | STAGE HOUSING |  | STS304 | STS316L | 1
2250 | IMPELLER |  | STS304 | STS316L | n
2410 | IMPELLER SPACER |  | STS304 | STS316L | 2n-1
2460A | SHAFT SLEEVE |  | STS304 | STS316L | 1
2460B | SEAL SPACER |  | STS304 | STS316L | 1
2460D | SHIM WASHER |  | STS316L |  | 1
2520 | RING KEEPER |  | STS316L |  | 1
2911A | SHAFT END WASHER |  | STS316L |  | 1
2911B | SEAL SPACER |  | STS316L |  | 1
3044 | STAGE HOUSING |  | STS304 | STS316L | 1
3400 | SHAFT SLEEVE |  | STS316L |  | 1
4200 | MECHANICAL SEAL |  | Carbon/Ceramics |  | 1
4213 | RING HOLDER |  | EPDM | Viton | 1
4610A/B/C | O RING |  | EPDM | Viton | 1/1/1
6515/6521 | PLUG |  | STS316L |  | 1/1
6545 | THRUST RING |  | STS316L |  | 2
9820 | MOTOR COOLING FAN |  | Plastic |  | 1
9822 | FAN COVER |  | Steel sheets |  | 1
9825 | TERMINAL BOX COVER |  | Plastic |  | 1
9860 | CAPACITOR |  | Polypropylene |  | 1
9902A | SCREW |  | Zinced steel |  | 8
9903A/C | SCREW |  | Zinced steel |  | 4/5
9923A | NUT |  | Zinced steel |  | 1
|  | TYPE |  | Multistage Horizontal Pump
|  | MODEL |  | MHi-Models
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of Mhi Type

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 57 | 105 | 126 | 149 | 162 | 176 | 178
Dis. Head | (m) | 32.8 | 28 | 22 | 18 | 12 | 8 | 4 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 32.8 | 28 | 22 | 18 | 12 | 8 | 4 | 1
Water Power | (㎾) | 0 | 0.26015 | 0.37653 | 0.36968 | 0.29144 | 0.21125 | 0.11475 | 0.029014
Shaft Power | (㎾) | 0.29704 | 0.53404 | 0.67782 | 0.70468 | 0.70547 | 0.69283 | 0.67466 | 0.64227
Pump Eff. | (%) | 0 | 48.7132 | 55.5501 | 52.4613 | 41.312 | 30.4906 | 17.0089 | 4.5174
Speed | (rpm) | 3505 | 3411 | 3347 | 3335 | 3327 | 3330 | 3336 | 3348
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.1 | 2.53 | 2.86 | 2.93 | 2.93 | 2.9 | 2.84 | 2.76
Motor Input | (㎾) | 0.376 | 0.676 | 0.858 | 0.892 | 0.893 | 0.877 | 0.854 | 0.813
Motor Eff. | (%) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 100 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 20 | (m) | Pole (P) | 4 | Freq.(Hz) | 60 | 25 | 25 | 0
Efficiency |  | (%) | Volt. (V) | 220/380 | Current(A) | 3.0/1.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 79 | Maker | WILO | Electric | 22 | 18
Item No. |  |  | Serial No. |  | Inspector | J.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | MHI-402I |  | Customer |  |  |  | 2 |  | 04.10.18
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification