## Datasheet
PUMP DATA SHEET
| Model | MHI406I | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 100 | ℓ/min (Ht=65m 일때) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 65 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 65 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 60 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 2200 | W | Impeller | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Shaft | STS316L
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | STS304
16 | Bore | Size(Dia) | Rating | Face | Position | Stage Housing | STS304
17 | Suction | 32mm |  | □ FF, □ RF | ■End □Top □Side | Shaft Sleeve | STS304
18 | Discharge | 25mm |  | □ FF, □ RF | ■Top, □Side
19 | Impeller Type | CLOSED | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6204ZZ | Thrust Bearing | 6305ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220/380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 2200W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type | MG1/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Multistage Horizontal Pump
MODEL |  | MHI406I
SERVICE
SCALE:N/S
OUTLINE DRAWING
of MHI TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
No. | Part name |  | Material |  | Q'NTY
|  |  | MHi00000 | MHi00000S
0000 | MOTOR |  | - |  | 1
1111 | CASING |  | STS304 | STS316L | 1
1150 | STAGE HOUSING |  | STS304 | STS316L | n-1
1154 | STAGE CENTERING |  | STS304 | STS316L | 1
1160 | STAGE HOUSING |  | STS304 | STS316L | 1
2250 | IMPELLER |  | STS304 | STS316L | n
2410 | IMPELLER SPACER |  | STS304 | STS316L | 2n-1
2460A | SHAFT SLEEVE |  | STS304 | STS316L | 1
2460B | SEAL SPACER |  | STS304 | STS316L | 1
2460D | SHIM WASHER |  | STS316L |  | 1
2520 | RING KEEPER |  | STS316L |  | 1
2911A | SHAFT END WASHER |  | STS316L |  | 1
2911B | SEAL SPACER |  | STS316L |  | 1
3044 | STAGE HOUSING |  | STS304 | STS316L | 1
3400 | SHAFT SLEEVE |  | STS316L |  | 1
4200 | MECHANICAL SEAL |  | Carbon/Ceramics |  | 1
4213 | RING HOLDER |  | EPDM | Viton | 1
4610A/B/C | O RING |  | EPDM | Viton | 1/1/1
6515/6521 | PLUG |  | STS316L |  | 1/1
6545 | THRUST RING |  | STS316L |  | 2
9820 | MOTOR COOLING FAN |  | Plastic |  | 1
9822 | FAN COVER |  | Steel sheets |  | 1
9825 | TERMINAL BOX COVER |  | Plastic |  | 1
9860 | CAPACITOR |  | Polypropylene |  | 1
9902A | SCREW |  | Zinced steel |  | 8
9903A/C | SCREW |  | Zinced steel |  | 4/5
9923A | NUT |  | Zinced steel |  | 1
|  | TYPE |  | Multistage Horizontal Pump
|  | MODEL |  | MHi-Models
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of Mhi Type

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 44.4 | 77.9 | 123 | 151 | 173 | 178 | 178.5
Dis. Head | (m) | 97.9 | 90 | 80 | 60 | 40 | 20 | 10 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.060032 | 0.1848 | 0.46071 | 0.69434 | 0.9114 | 0.96484 | 0.97027
Total Head | (m) | 97.9 | 90.06 | 80.1848 | 60.4607 | 40.6943 | 20.9114 | 10.9648 | 2.4703
Water Power | (㎾) | 0 | 0.65178 | 1.0182 | 1.2122 | 1.0016 | 0.58968 | 0.31813 | 0.071874
Shaft Power | (㎾) | 0.83476 | 1.4432 | 1.8311 | 2.1131 | 2.1008 | 1.968 | 1.8696 | 1.7892
Pump Eff. | (%) | 0 | 45.1623 | 55.6051 | 57.3638 | 47.6766 | 29.9634 | 17.0162 | 4.017
Speed | (rpm) | 3546 | 3504 | 3474 | 3448 | 3451 | 3462 | 3470 | 3475
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.58 | 3.42 | 4.09 | 4.58 | 4.54 | 4.3 | 4.12 | 3.99
Motor Input | (㎾) | 1.018 | 1.76 | 2.233 | 2.577 | 2.562 | 2.4 | 2.28 | 2.182
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 100 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 65 | (m) | Pole (P) | 4 | Freq.(Hz) | 60 | 30 | 25 | 0
Efficiency |  | (%) | Volt. (V) | 220/380 | Current(A) | 8.9/5.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | WILO | Electric | 22 | 18
Item No. |  |  | Serial No. |  | Inspector | J.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | MHI-406I |  | Customer |  |  |  | 2 |  | 04.10.18
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification