## Datasheet
PUMP DATA SHEET
| Model | PB-138MA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 40 ℓ/min | at Ht=0.5m
7 | Pumping Temp | 0~40 ℃ | Suct.Head | 0 | m
8 | Sp. Gr. @P.T | 1 | Disch.Press | 12 | m
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 12 | m
10 | Visc @P.T | Cp
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 25 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 135 | W | Impeller | NORYL
14 | Speed | 3400 rpm | NPSHre |  | mAq | Valve | NORYL
15 | Rotation | □ CW, ■ CCW | (viewed from pump head) |  |  | Shaft | STS410
16 | Union | Size(Dia) |  | Position |  | Casing | GC200+Coating
17 | Suction | 15mm |  | □End □Top ■Side |  | Union | C3771BD
18 | Discharge | 15mm |  | □Top, ■Side
19 | Impeller Type | Centrifugal | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 3 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | - Kg/㎠ | - Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 608ZZ | Thrust Bearing | 608ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO PUMPS Ltd. |  |  |  | Shaft | Set(S)
30 | Type | ODP |  |  |  | M/Seal | Set(S)
31 | Power | 135W |  |  |  | Casing | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation | □ B | ■ E | Valve | Set(S)
33 | ACCESSORIES |  |  |  |  | Union | Set(S)
34 | □Base Plate | □ Cast Iron | □ Plastic | □ Steel Plate | □ Drain Rim |  | Set(S)
35 | ■Unions | 15mm |  |  |  |  | Set(S)
36 | □Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No |  | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press ■No |  |  |  |  | Set(S)
38 | □Plug for Priming & Screw for Drain | [5 empty] | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  |  | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 8 |  | Set(S)
41 | Mechanical Seal | Type | EA103-08 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | 1.4 Kg
43 | □ Companion Flange |  |  |  |  | Driver | 2.6 Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 4.0 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 45 |  | MOTOR | OUTPUT |  |  |  | W | 135
| TOTAL HEAD | m | 13 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION UNION | mm | Ø | 15 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE UNION | mm | Ø | 15 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3400
| LIQUID | WATER |  |  |  | TYPE |  |  |  | 1 PHASE INDUCTION
| MAKER | WILO |  |  |  | MAKER |  |  |  | OH SUNG
(unit : mm)
[7 empty] | TYPE |  | WESTCO PUMP
[7 empty] | MODEL |  | PB-138MA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PB TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR | - |  |  |  | 1
2 | MECHANICAL SEAL | CARBON/CERAMIC |  |  |  | 1
3 | BOLT | SM20C |  |  |  | 2
4 | IMPELLER | NORYL |  |  |  | 1
5 | O-RING | NBR607 |  |  |  | 1
6 | CASING | GC200+COATING |  |  |  | 1
7 | UNION ASSY | C3771BD |  |  |  | 1
8 | VALVE ASSY | NORYL |  |  |  | 2
9 | VALVE COVER | NORYL / STS |  |  |  | 1
10 | SCREW | SM20C |  |  |  | 1
11 | CAPACITOR | - |  |  |  | 1
12 | CAPACITOR COVER | PP |  |  |  | 1
13 | SCREW | SM20C |  |  |  | 1
14 | ROCKER SWITCH | - |  |  |  | 1
15 | FAN | PBT |  |  |  | 1
16 | FAN COVER | ABS |  |  |  | 1
|  |  | TYPE |  | CENTRIFUGAL PUMP
|  |  | MODEL |  | PB-138MA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PB TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.8 | 19.3 | 31.9 | 37.8 | 42.3 | 46.4 | 49.2
Dis. Head | (m) | 13.4 | 12 | 10 | 8 | 6 | 4 | 2 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 13.4 | 12 | 10 | 8 | 6 | 4 | 2 | 0.5
Water Power | (㎾) | 0 | 0.021125 | 0.031459 | 0.041598 | 0.036968 | 0.02758 | 0.015126 | 0.0040098
Shaft Power | (㎾) | 0.08905 | 0.1053 | 0.1196 | 0.1404 | 0.15275 | 0.1625 | 0.1716 | 0.17745
Pump Eff. | (%) | 0 | 20.0615 | 26.3035 | 29.6279 | 24.2019 | 16.9721 | 8.8149 | 2.2597
Speed | (rpm) | 3470 | 3418 | 3371 | 3283 | 3228 | 3179 | 3113 | 3078
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.71 | 0.82 | 0.91 | 1.04 | 1.12 | 1.18 | 1.24 | 1.28
Motor Input | (㎾) | 0.137 | 0.162 | 0.184 | 0.216 | 0.235 | 0.25 | 0.264 | 0.273
Motor Eff. | (%) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 40 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.135 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 0.5 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 15 | 15
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 65 | Maker | WILO | Electirc | 25 | 24
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PB-138MA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification