## Datasheet
PUMP DATA SHEET
Model | PB-351MA | Title |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Date Issued
Item No. |  |  | Plant Name
Service |  |  | Quantity |  | Location | ■In, □Out
OPERATING CONDITION
Liquid | Water | Flow | 80 ℓ/min | at Ht=0.5m
Pumping Temp | 0~80 ℃ | Suct.Head | 0 | m
Sp. Gr. @P.T | 1 | Disch.Press | 21 | m (max.)
Vap. Press @P.T | Kg/㎠A | Total Head | 21 | m
Visc @P.T | Cp
PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
■ Horizontal | □ Vertical | Efficiency | 25 | % | (Parts' Name) | Symbol(KS)
Number of Stages | 1 Stage | Rated Power | 350 | W | Impeller | NORYL
Speed | 3450 rpm | NPSHre |  | mAq | Valve | NORYL
Rotation | □ CW, ■ CCW | (viewed from pump head) |  |  | Shaft | STS410
Union | Size(Dia) |  | Position |  | Casing | GC200+Coating
Suction | 25mm (1") |  | □End □Top ■Side |  | Union
Discharge | 25mm (1") |  | □Top, ■Side
Impeller Type | Centrifugal | ■Single Suct. | □Double Suct. | HYDROSTATIC
Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 6 Kg/㎠ | 3 Min.
Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | - Kg/㎠ | - Min.
Shaft Sleeve | □Yes, ■No
Mounting | □ Foot | □ Centerline | ■ Bracket | TESTING
Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
Radial Bearings | 6201ZZ | Thrust Bearing | 6201ZZ | Hydrostatic | ■ Yes □ No | □Yes ■No
PUMP DRIVER |  |  |  |  | SPARE PARTS
Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
Maker | WILO PUMPS LTD. |  |  |  | Shaft | Set(S)
Type | TEFC (IPX4) |  |  |  | M/Seal | Set(S)
Power | 350W |  |  |  | Casing | Set(S)
Pole & Speed | 2 p 3450 rpm | Insulation | ■ B | □ E | Valve | Set(S)
ACCESSORIES |  |  |  |  | Union | Set(S)
□Base Plate | □ Cast Iron | □ Plastic | □ Steel Plate | □ Drain Rim |  | Set(S)
□Unions | [5 empty] | Set(S)
□Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No |  | Set(S)
□Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press ■No |  |  |  |  | Set(S)
□Plug for Priming & Screw for Drain | [5 empty] | Set(S)
□Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  |  | Set(S)
| Maker | N.E.K | Model & Size | Φ 12 |  | Set(S)
Mechanical Seal | Type | EA104-12 | Cooler | □Yes, ■No | WEIGHT
[5 empty] | Pump / Bed | 2.6 Kg
□ Companion Flange |  |  |  |  | Driver | 4.7 Kg
□ Special Tools |  |  |  |  | Total Wt. | 7.3 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | max.80 |  | MOTOR | OUTPUT |  |  |  | W | 350
| TOTAL HEAD | m | 21 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION | mm | Ø | 25 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | 1 PHASE INDUCTION
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
`
[7 empty] | TYPE |  | CENTRIFUGAL PUMP
[7 empty] | MODEL |  | PB-351MA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PB TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | CENTRIFUGAL PUMP
MODEL |  | PB-351MA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PB TYPE
1
9
10
11
7
4
5
3
6
2
20
14
12
23
16
17
18
19
20
21
22
8
13
15

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 26 | 34.3 | 49.2 | 55.2 | 66.5 | 72 | 80.5
Dis. Head | (m) | 21.7 | 18 | 16 | 12 | 10 | 6 | 4 | 1.7
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 27.7 | 24 | 22 | 18 | 16 | 12 | 10 | 7.7
Water Power | (㎾) | 0 | 0.10171 | 0.123 | 0.14435 | 0.14396 | 0.13007 | 0.11736 | 0.10104
Shaft Power | (㎾) | 0.2653 | 0.3066 | 0.3164 | 0.3304 | 0.3318 | 0.3325 | 0.3325 | 0.3304
Pump Eff. | (%) | 0 | 33.1742 | 38.8748 | 43.6903 | 43.3881 | 39.12 | 35.2962 | 30.5798
Speed | (rpm) | 3460 | 3430 | 3413 | 3403 | 3398 | 3395 | 3395 | 3395
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.76 | 2.02 | 2.09 | 2.18 | 2.19 | 2.21 | 2.18 | 2.18
Motor Input | (㎾) | 0.379 | 0.438 | 0.452 | 0.472 | 0.474 | 0.475 | 0.475 | 0.472
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.490 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 0.5 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 25 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 2.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Electirc
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PB-351MA |  | Customer |  |  |  | 1 |  | 2012.11.06
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification