## Datasheet
PUMP DATA SHEET
| Model | PB-601SMA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 50 ℓ/min | at Ht=15m
7 | Pumping Temp | 0~60 ℃ | Suct.Head | 0 | m (3m with foot valve at the end of suction pipe)
8 | Sp. Gr. @P.T | 1 | Disch.Press | 18 | m (Shutoff Head 28m)
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 18 | m
10 | Visc @P.T | Cp | Automatic | On at1.8kgf/㎠ by Pressure switch & Off at5ℓ/min by Flow switch
11 | PERFORMANCE AND CONSTRUCTIONS |  |  |  |  | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 25 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 600 | W | Impeller | NORYL
14 | Speed | 3450 rpm | NPSHre |  | mAq | Valve | NORYL
15 | Rotation | □ CW, ■ CCW | (viewed from pump head) |  |  | Shaft | STS410
16 | Flange | Size(Dia) |  | Position |  | Casing | Coated GC200
17 | Suction | 32mm(1 1/4") |  | □End □Top ■Side |  | Terminal Box | ABS
18 | Discharge | 32mm(1 1/4") |  | □Top, ■Side |  | Flange | GC200
19 | Impeller Type | Centrifugal | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 6 Kg/㎠ | 5 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal |  | Pressure Tank | 9 Kg/㎠ | 5 Min.
22 | Shaft Sleeve | □Yes, ■No
23 | Mounting | □ Foot | □ Centerline | ■ Bracket | TESTING
24 | Lubrication Type | ■ Grease | □ Oil Bath |  | (Items) | (self test) | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | ■ No. Cooling | Run Perform. | ■ Yes □ No | □Yes ■No
26 | Radial Bearings | 6302zz | Thrust Bearing | 6202zz | Hydrostatic | ■ Yes □ No | □Yes ■No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO PUMPS LTD. |  |  |  | Shaft | Set(S)
30 | Type | TEFC (IPX4) |  |  |  | M/Seal | Set(S)
31 | Power | 600W |  |  |  | Casing | Set(S)
32 | Pole & Speed | 2 p 3450 rpm | Insulation | ■ B | □ E | Valve | Set(S)
33 | ACCESSORIES |  |  |  |  | Union | Set(S)
34 | □Base Plate | □ Cast Iron | □ Plastic | □ Steel Plate | □ Drain Rim |  | Set(S)
35 | □Flange | □ Union | ■ Oval |  |  |  | Set(S)
36 | □Coupling | □ Sun Flex | □ WOODS | □ Grid | ■No |  | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound |  | □Suct.Press | □Disch.Press ■No |  | Set(S)
38 | □Plug for Priming & Screw for Drain |  |  | ■Yes | □No |  | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping | ■No |  |  | Set(S)
40 |  | Maker | N.E.K | Model & Size | Φ 15 |  | Set(S)
41 | Mechanical Seal | Type | EA104-15 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | 5.7 Kg
43 | □ Companion Flange |  | ■Yes | □No |  | Driver | 7.8 Kg
44 | □ Special Tools |  | □Yes | ■No |  | Total Wt. | 13.5 kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 65 |  | MOTOR | OUTPUT |  |  |  | W | 600
| TOTAL HEAD | m | 18 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION Flange | mm | Ø | 32 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE Flange | mm | Ø | 32 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | 1 PHASE INDUCTION
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | CENTRIFUGAL PUMP
[7 empty] | MODEL |  | PB-601SMA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PB TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty(EA)
1 | MOTOR ASSY | 1PHASE 220V 60Hz |  |  |  | 1
2 | CASING | GC200 COATED |  |  |  | 1
3 | IMPELLER | NORYL |  |  |  | 1
4 | FAN | PBT |  |  |  | 1
5 | FAN COVER | ABS |  |  |  | 1
6 | CAPACITOR | 15㎌/420VAC |  |  |  | 1
8 | TERMINAL BASE | ABS |  |  |  | 1
9 | TERMINAL COVER | ABS |  |  |  | 1
10 | CHECK VALVE ASSY | Bronze/Noryl/Magnet |  |  |  | 1
11 | PRESSURE SWITCH | On:1.8kgf/㎠ Off:2.4kgf/㎠ |  |  |  | 1
12 | PRESSURE TANK | SCP/NBR |  |  |  | 1
13 | SUPPORTER | ABS |  |  |  | 1
14 | DRAIN SCREW | M6
15 | HOPPER CAP | Bronze |  |  |  | 1
|  |  | TYPE |  | CENTRIFUGAL PUMP
|  |  | MODEL |  | PB-601SMA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PB TYPE
Capacitor
Terminal
Base
Pressure
Switch
Terminal
Cover
Fan
Cover
Fan
Casing
Impeller
Pressure
Tank
Supporter
Check Valve A’ssy
Drain
Screw
Hopper Cap
Flange

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 12.2 | 28.1 | 38.2 | 52.9 | 65.9 | 71.2 | 78.6
Dis. Head | (m) | 28.8 | 27 | 24 | 21 | 15 | 9 | 6 | 1.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 28.8 | 27 | 24 | 21 | 15 | 9 | 6 | 1.1
Water Power | (㎾) | 0 | 0.053692 | 0.10993 | 0.13076 | 0.12934 | 0.096675 | 0.069634 | 0.014093
Shaft Power | (㎾) | 0.3445 | 0.3835 | 0.4264 | 0.44395 | 0.46865 | 0.47645 | 0.48035 | 0.48165
Pump Eff. | (%) | 0 | 14.0006 | 25.7803 | 29.4535 | 27.5985 | 20.2908 | 14.4964 | 2.926
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.86 | 3.06 | 3.3 | 3.41 | 3.55 | 3.61 | 3.62 | 3.64
Motor Input | (㎾) | 0.53 | 0.59 | 0.656 | 0.683 | 0.721 | 0.733 | 0.739 | 0.741
Motor Eff. | (%) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.325 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 15 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 32 | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 65 | Maker | WILO | Electirc | 28 | 24
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PB-601SMA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification