## Datasheet(PBE-203LMA)
PUMP DATA SHEET
| Model | PBE-203LMA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 50 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 25 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 25 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 40 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 3 Stage | Rated Power | 750 | W | Impeller | STS304
14 | Speed | 3450 rpm | NPSHre |  | mAq | Shaft | STS420
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Middle Casingt | STS304
16 | Flange | Size(Dia) | Rating | Face | Position | Casing | STS304
17 | Suction | 25mm |  | □ FF, □ RF | □End □Top ■Side | Diffuser | STS304
18 | Discharge | 25mm |  | □ FF, □ RF | ■Top, □Side
19 | Impeller Type | Closed | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 6 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6320ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 750W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3450 rpm | Insulation Class | F Class |  | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker |  | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type |  | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 30 Kg

## Outline Drawing(PBE-203LMA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 50 |  | MOTOR | OUTPUT |  |  |  | W | 750
| TOTAL HEAD | m | 25 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø | 25 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | ONE PHASE INDUCTION
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
※ Pressure Tank Size : 50ℓ
[7 empty] | TYPE |  | 1 TANK BOOSTER
[7 empty] | MODEL |  | PBE-203LMA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PBE TYPE

## Sectional Drawing(PBE-MHi)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME |  | MATERIALS |  |  |  |  | Q'ty(EA) | Remark
|  |  | KS | ASTM | DIN
1 | MOTOR |  | - | - | - |  |  | 1
2 | TERMINAL COVER |  | PLASTIC | - | - |  |  | 1
3 | END BRACKET(A) |  | ALDC | - | - |  |  | 1
4 | PRESSURE SWITCH |  | - | - | - |  |  | 1
5 | NIPPLE |  | BrC3 | - | - |  |  | 1
6 | MECHANICAL SEAL |  | NBR+CARBON+CERAMIC | - | - |  |  | 1
7 | IMPELLER SET |  | STS304 | - | - |  |  | *Stages
8 | CASING |  | STS304 | - | - |  |  | 1
9 | SHAFT |  | STS304 | - | - |  |  | 1
10 | DRAIN CAP |  | STS304 | - | - |  |  | 2
11 | CHECK VALVE |  | C3771BD+PP | - | - |  |  | 1
12 | PRESSURE TANK |  | - | - | - |  |  | 1
13 | TANK LEG |  | PLASTIC | - | - |  |  | 1
14 | FLEXIBLE HOSE |  | STS304+BrC3 | - | - |  |  | 1
Model |  | *Stages | Tank Volume |  | TYPE |  | Booster Pump
PBE-203LMA |  | 3 | 50ℓ
PBE-402LMA |  | 2 | 50ℓ |  | MODEL
PBE-202LMA |  | 2 | 20ℓ |  | SERVICE
PBE-403LMA |  | 3 | 50ℓ |  | SCALE:N/S
SECTIONAL DRAWING
of PBE TYPE
1
2
3
4
5
6
7
9
10
8
11
12
14
13

## Test Report(PBE-203LMA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.3 | 35.5 | 47.5 | 60 | 72 | 82.5 | 96 | 107
Dis. Head | (m) | 45.2 | 40 | 35 | 30 | 25 | 20 | 15 | 10 | 5.6
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 45.2 | 40 | 35 | 30 | 25 | 20 | 15 | 10 | 5.6
Water Power | (㎾) | 0 | 0.13236 | 0.20253 | 0.23228 | 0.2445 | 0.23472 | 0.20171 | 0.15648 | 0.09767
Shaft Power | (㎾) | 0.63024 | 0.72384 | 0.75972 | 0.7839 | 0.79326 | 0.7917 | 0.7722 | 0.7488 | 0.72306
Pump Eff. | (%) | 0 | 18.2853 | 26.6582 | 29.6307 | 30.8222 | 29.6476 | 26.1218 | 20.8974 | 13.5078
Speed | (rpm) | 3420 | 3383 | 3340 | 3305 | 3286 | 3283 | 3287 | 3297 | 3299
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.8 | 4.2 | 4.43 | 4.58 | 4.62 | 4.59 | 4.49 | 4.35 | 4.22
Motor Input | (㎾) | 0.808 | 0.928 | 0.974 | 1.005 | 1.017 | 1.015 | 0.99 | 0.96 | 0.927
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 25 | 25 | 0
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 5.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | WILO | Turbin | 12 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PBE-203LMA |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification