## Datasheet
PUMP DATA SHEET
| Model | PBi-406UA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid |  | Flow | 130 | ℓ/min (Ht=60m 일때) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 0 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 99 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 99 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 45 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 6 Stage | Rated Power | 2200 | W | Impeller | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Shaft | STS316L
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | STS304
16 | Bore | Size(Dia) | Rating | Face | Position | Stage Housing | STS304
17 | Suction | 32mm |  | □ FF, □ RF | ■End □Top □Side | Shaft Sleeve | STS304
18 | Discharge | 25mm |  | □ FF, □ RF | ■Top, □Side
19 | Impeller Type | CLOSED | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath |  | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6302ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 2200W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type | MG1/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 20Kg

## Dimension(PBI)
Sheet No.
CUSTOMER
ITEM No.
DATE
|  |  | 모델명 | Dimension(mm) | [8 empty] | 중량
|  |  |  | H | H1 | H2 | H3 | L | L1 | L2 | ΦD1 | ΦD2 | (kg)
|  |  | PBI-203MA | 610 | 90 | 120 | 380 | 385 | 185 | 109.5 | 1" | 1" | 13
|  |  | PBI-205MA | 610 | 90 | 120 | 380 | 430 | 235 | 157.5 | 1" | 1" | 15
|  |  | PBI-402MA | 610 | 90 | 120 | 380 | 385 | 185 | 109.5 | 1 1/4" | 1" | 14
|  |  | PBI-403MA | 610 | 90 | 120 | 380 | 385 | 185 | 109.5 | 1 1/4" | 1" | 17
|  |  | PBI-404MA | 610 | 90 | 120 | 380 | 425 | 225 | 157.5 | 1 1/4" | 1" | 17
|  |  | PBI-405MA | 610 | 90 | 120 | 380 | 425 | 225 | 157.5 | 1 1/4" | 1" | 18
|  |  | PBI-406UA | 580 | 100 | 104 | 465 | 484 | 276 | 181.5 | 1 1/4" | 1" | 20
|  |  | PBI-802MA | 630 | 90 | 120 | 385 | 390 | 190 | 121.5 | 1 1/2" | 1 1/4" | 18
|  |  | PBI-803MA | 630 | 90 | 120 | 385 | 390 | 190 | 121.5 | 1 1/2" | 1 1/4" | 19
|  |  | PBI-804UA | 610 | 100 | 104 | 465 | 484 | 276 | 181.5 | 1 1/2" | 1 1/4" | 21
TYPE |  | Multistage Horizontal Pump
MODEL |  | PBI-406UA
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PBI-Model

## Sectional(PBI)
Sheet No.
CUSTOMER
ITEM No.
DATE
Cls. | Part Name | Specification |  | Quantity | Remarks
1 | Motor Assembly | 3phase 380V 60Hz |  | 1
2 | Motor Supporter | ABS(HI-100) |  | 1
3 | Fan | PBT(GP-2200) |  | 1
4 | Fan Cover | SCP or ABS(HI-100) |  | 1
5 | Base Plate | SCP |  | 1
6 | Casing | STS304 |  | 1
7 | Drain Plug | STS316L |  | 1
8 | Priming Plug | STS316L |  | 1
9 | Union Assembly | Brass or STS304 |  | 1
10 | Check Valve | STS304 |  | 1
11 | Cross Nipple | Brass or STS304 |  | 1
12 | Pressure Tank | SCP/Rubber |  | 1
13 | Pressure Gauge | 16bar |  | 1
14 | Inverter Cover | ABS(AF-305F) |  | 1
15 | Inverter Assembly | - |  | 1
16 | Inverter Base | ABS(AF-305F) |  | 1
17 | Transmitter | 16bar |  | 1
|  |  | TYPE |  | Multistage Horizontal Pump
|  |  | MODEL |  | PBI-406UA
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of PBI-Model
15
7
1
2
3
4
5
8
9
10
6
11
12
13
14
16
17

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 55 | 100 | 130 | 156 | 178 | 182 | 182
Dis. Head | (m) | 99 | 90 | 75 | 60 | 40 | 20 | 10 | 1.7
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.11164 | 0.36906 | 0.62371 | 0.89814 | 1.1693 | 1.2225 | 1.2225
Total Head | (m) | 99 | 90 | 75 | 60 | 40 | 20 | 10 | 1.7
Water Power | (㎾) | 0 | 0.80685 | 0.25 | 1.2714 | 1.0171 | 0.58028 | 0.15 | 0.050432
Shaft Power | (㎾) | 0.8077 | 1.622 | 2.0861 | 2.2353 | 2.2927 | 2.1172 | 2.1 | 2.0024
Pump Eff. | (%) | 0 | 49.7454 | 11.9842 | 56.8778 | 44.363 | 27.4074 | 7.1428 | 2.5185
Speed | (rpm) | 3543 | 3502 | 3455 | 3439 | 3437 | 3446 | 3452 | 3457
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.06 | 5.34 | 6.47 | 6.88 | 7.03 | 6.4 | 6.34 | 6.01
Motor Input | (㎾) | 0.985 | 1.978 | 2.544 | 2.726 | 2.796 | 2.582 | 2.561 | 2.442
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 125 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 32 | 25 | 0
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 5.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | WILO | Turbin | 18 | 13
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PBI-406UA |  | Customer |  |  |  | 1 | 36
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716
Suc. Head | m | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Suc. Head | m | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Vacuum | mmhg | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716 | 220.716
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Data (hidden)
No. | Model | Capa.(ℓ/min.) | Head(m) | Power Supply | Output | Disharge | Pole | RPM | Impeller Type | Suction | Casing Mat'l | Impeller Mat'l | Shaft Mat'l | Flange Mat'l | Capa1 | Capa2 | Capa3 | Capa4 | Capa5 | Head1 | Head2 | Head3 | Head4 | Head5 | SP1 | SP2 | SP3 | SP4 | SP5 | Eff1 | Eff2 | Eff3 | Eff4 | Eff5 | 380V Amp.
1 | PU-756M | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
2 | PW-K130MA | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
3 | PW-409MA | 32(at Ht 12m) | 30 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.1 | 16.7 | 28.5 | 38 | 55 | 46 | 36 | 21 | 9 | 0.6 | 0.55 | 0.47 | 0.37 | 0.3 | 0 | 11.12 | 20.82 | 26.38 | 18.59 | 8
4 | PW-405M | 40(at Ht 12m) | 36 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 10 | 31 | 41 | 46 | 53 | 46 | 26 | 16 | 9.5 | 0.73 | 0.65 | 0.46 | 0.39 | 0.34 | 0 | 11.48 | 28.68 | 27.55 | 20.94 | 8
5 | PW-804MA | 45(at Ht 12m) | 33 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 15 | 32 | 46 | 50 | 74 | 56 | 34 | 16 | 12 | 0.99 | 0.85 | 0.67 | 0.54 | 0.52 | 0 | 16.14 | 26.51 | 22.15 | 18.88 | 8