## Datasheet(PBI)
PUMP DATA SHEET
Model |  | PBI-Series |  |  |  | Title |  |  |  |  | Sheet No.
Customer | [5 empty] | Agent No.
Location | [5 empty] | Date Issued
Item No. | [5 empty] | Plant Name
Service | [5 empty] | Quantity |  |  |  |  | Location |  | ■ In, □ Out
OPERATING CONDITION
Environment |  | 0~40 ℃ |  |  | Humidity |  | 95% max |  |  | Altitude |  |  | 1,000m max
Delivery Pressure |  | max.10 bar |  |  | No. of starts |  | Motor<1.5kW : 80/hr 1.5kW<Motor<2.2kW : 50/hr Motor>2.2kW : 20/hr
Running time |  | 12,000hr |  |  | Granulometry |  | Ø 0.5mm max |  |  | Kinematic viscosity |  |  | equivalent to water
Density |  | 1.03 kg/dm3 in standard |  |  | PH |  | STS304 = 6 to 9.5 (STS316L =5 to 12)
PERFORMANCE AND CONSTRUCTIONS
|  | Model | PBI- 203MA | PBI- 205MA | PBI- 402MA | PBI- 403MA | PBI- 404MA | PBI- 405MA | PBI- 802MA | PBI- 803MA
Classification
Power Source (V/ph/Hz) |  |  | 220/1/60
Motor (V/Phase/Hz) |  |  | 220/3/60
Motor Input(kW) |  |  | 0.92 | 1.55 | 0.92 | 1.55 | 2.17 | 2.38 | 2.17 | 2.38
Motor Output(kW) |  |  | 0.75 | 1.1 | 0.75 | 1.1 | 1.5 | 1.85 | 1.5 | 1.85
Inverter Output(kW) |  |  | 0.75 | 1.5 | 0.75 | 1.5 |  | 2.2 | 1.5 | 2.2
Inverter Capacity(KVA) |  |  | 2.64 | 3.3 | 2.64 | 3.3 |  | 4.4 | 3.3 | 4.4
Inverter Input Frequency(Hz) |  |  | 50~60
Inverter Output Freq.(Hz) |  |  | max.60
Rotational Speed(rpm) |  |  | 1,200~3,400
Current (A) | Pump | 1 phase | 5.1 | 9.3 | 5.1 | 9.3 | 11.7 | 13.3 | 11.7 | 13.3
| Motor | 3 phase | 3 | 5.5 | 3 | 5.5 | 6.9 | 7.8 | 6.9 | 7.8
Pump Shut off Head(m) |  |  | 47 | 80 | 30 | 46 | 62 | 80 | 30 | 48
Flow (m3/hr) | Rated Flow | Q | 2 |  | 4 |  |  |  | 8
|  | at H(m) | 35 | 60 | 22 | 35 | 45 | 60 | 22 | 35
Piping(mm) |  | Suct. | 25 |  | 30 |  |  |  | 40
|  | Disch. | 25 |  | 25 |  |  |  | 30
No. of Impeller Stages |  |  | 3 | 5 | 2 | 3 | 4 | 5 | 2 | 3
Diameter of Impeller(mm) |  |  | 99 | 99 | 98.5 | 98.5 | 98.5 | 98.5 | 100.5 | 100.5
Bearing | Pump Side |  | 6302 |  |  |  | 6304
| Fan Side |  | 6202 |  |  |  | 6204
Cable Gland |  |  | PG13.5 | PG13.5 | PG13.5 | PG13.5 | PG13.5 | PG13.5 | PG13.5 | PG13.5
Weight (kg) |  |  | 10.5 | 12.1 | 10.5 | 12.1 | 14.6 | 15.5 | 13.9 | 16
Mounting Position |  |  | ■ Hotizontal, □ Vertical |  |  |  |  | Suction Head(m) |  |  | Non self priming
Motor Maker |  |  | WILO (in Korea) |  |  |  |  | Insulation Class |  |  | B
Shaft Seal |  |  | □ G/Packing, ■ M/Seal |  |  |  |  | Protecting Index |  |  | IPX4
Speed |  |  | 3,400 rpm |  |  |  |  | Rotation |  |  | □ CW, ■ CCW (viewed from pump Head)
Impeller Type |  |  | Centrifugal |  |  |  |  | Flow Direction |  |  | ■ Radial, □ Mixed, □ Axial
Lubrication Type |  |  | ■ Grease, □ Oil Bath |  |  |  |  | Cooling |  |  | □ Stuff. Box, □ B/R Housing, ■ No cooling
TESTING | [7 empty] | HYDROSTATIC
( Items ) |  | ( Self test ) |  |  | ( Witness ) |  |  | Casing |  |  | 20 Kg/cm2 |  | 3 min
Run Performal |  | ■ Yes, □ No |  |  | □ Yes, ■ No |  |  | Pressure Tank |  |  | 25 Kg/cm2 |  | 3 min
Hydrostatic |  | ■ Yes, □ No |  |  | □ Yes, ■ No
MECHANICAL SEAL
TYPE |  |  | Ø on Shaft |  | Fitting Dimension |  | Service Limits |  |  | Materials
[10 empty] | Diaphragm |  | Spring |  | Cup Gasket
Burgmann MG1/14 -G606-U3BEGG |  |  | 14 |  | 23,6±1mm |  | P ≤ 16 bar, -20℃< T <120℃ |  |  | EPDM |  | AISI 316TI |  | EPDM
Burgmann MG1/14 -G606-U3BVGG |  |  | 14 |  | 23,6±1mm |  | P ≤ 16 bar, -15℃< T <90℃ |  |  | EPDM |  | AISI 316TI |  | EPDM
BT TEKO BT-A3 -NU 14 BVEGG |  |  | 14 |  | 22,1±0.8mm |  | P ≤ 10 bar, -15℃< T <110℃ |  |  | VITON |  | AISI 316 |  | VITON
Burgmann RMG1/14 -G6-Q11QE3GG |  |  | 14 |  | 23,6±1mm |  | P ≤ 25 bar, -20℃< T <90℃ |  |  | EPDM |  | AISI 316TI |  | EPDM
ACCESSORIES
■ Base plate |  |  | □ Drain Rim |  |  | □ Foundation Bolts & Nuts |  |  | ■ Plug for Priming & Screw for Drain
Coupling |  |  | □ Sun Flex □ Woods □ Grid ■ No | [5 empty] | □ Sealing Flushing Pipe □ Cooling Piping ■ No
Press. Gauge |  |  | □ Suct. Vacuum □ Suct. Compound □ Suct. Press ■ Disch. Press □ No
□ Companion Flange
□ Special Tools
SPARE PARTS
Impeller |  | Set(S) |  | Shaft Spacer |  | Set(S) |  | Shaft |  | Set(S) |  | Nipple |  | Set(S)
Bearing |  | Set(S) |  | Diffuser |  | Set(S) |  | M/Seal |  | Set(S) |  | Inverter |  | Set(S)
Casing O-Ring |  | Set(S) |  | Check Valve |  | Set(S) |  | Union |  | Set(S) |  | Sensor |  | Set(S)
Name Plate |  | Set(S) |  | Pressure Tank |  | Set(S) |  | Pressure Gauge |  | Set(S) |  | Terminal Box |  | Set(S)

## Dimension(PBI)
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Multistage Horizontal Pump
MODEL |  | PBI-Model
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PBI-Model

## Sectional(PBI)
Sheet No.
CUSTOMER
ITEM No.
DATE
Cls. | Part Name | Specification |  | Quantity | Remarks
1 | Motor Assembly | 3phase 220V 60Hz |  | 1
2 | Motor Supporter | ABS(HI-100) |  | 1
3 | Fan | PBT(GP-2200) |  | 1
4 | Fan Cover | SCP or ABS(HI-100) |  | 1
5 | Base Plate | SCP |  | 1
6 | Casing | STS304 |  | 1
7 | Drain Plug | STS316L |  | 1
8 | Priming Plug | STS316L |  | 1
9 | Union Assembly | Brass or STS304 |  | 1
10 | Check Valve | STS304 |  | 1
11 | Cross Nipple | Brass or STS304 |  | 1
12 | Pressure Tank | SCP/Rubber |  | 1
13 | Pressure Gauge | 16bar |  | 1
14 | Inverter Cover | ABS(AF-305F) |  | 1
15 | Inverter Assembly | - |  | 1
16 | Inverter Base | ABS(AF-305F) |  | 1
17 | Transmitter | 16bar |  | 1
18 | Power Cord | PNCT 3C |  | 1
|  |  | TYPE |  | Multistage Horizontal Pump
|  |  | MODEL |  | PBI-Model
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of PBI-Model
7
1
2
3
4
5
8
9
10
6
11
12
13
14
15
16
17
18

## TestReport
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA | [9 empty] | Q1 | Q2 | Q = ?
Capacity | (㎥/min) | 0 | 0.0701 | 0.136 | 0.17 | 0.199 | 0.223 | 0.247 | 0.257 | 0.107 | 0.163 | 0.133
Dis. Head | (m) | 33.5 | 30 | 24 | 20 | 15 | 10 | 5 | 2.2 | #N/A | #N/A | #N/A
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
Speed Head | (m) | 0 | 0.095281 | 0.35863 | 0.56036 | 0.76785 | 0.96423 | 1.1829 | 1.2807 | #N/A | #N/A | #N/A
Total Head | (m) | 33.5 | 30.0953 | 24.3586 | 20.5604 | 15.7679 | 10.9642 | 6.1829 | 3.4807 | #N/A | #N/A | #N/A
Water Power | (kW) | 0 | 0.34388 | 0.53998 | 0.56973 | 0.51146 | 0.39854 | 0.24893 | 0.14581 | #N/A | #N/A | #N/A
Shaft Power | (kW) | 0.41464 | 0.7373 | 0.9928 | 1.0811 | 1.1373 | 1.1556 | 1.1534 | 1.1498 | #N/A | #N/A | #N/A
Pump Eff. | (%) | 0 | 46.6401 | 54.3898 | 52.6974 | 44.97 | 34.4879 | 21.5824 | 12.6818 | #N/A | #N/A | #N/A
Speed | (rpm) | 3528 | 3420 | 3326 | 3286 | 3256 | 3233 | 3233 | 3232 | #N/A | #N/A | #N/A
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | #N/A | #N/A | #N/A
Current | (A) | 3.74 | 6.32 | 8.24 | 8.93 | 9.33 | 9.5 | 9.5 | 9.43 | #N/A | #N/A | #N/A
Motor Input | (kW) | 0.568 | 1.01 | 1.36 | 1.481 | 1.558 | 1.583 | 1.58 | 1.575 | #N/A | #N/A | #N/A
Motor Eff. | (%) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | #N/A | #N/A | #N/A
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.133 | (㎥/min) | Phase(Φ) | 1 | Output(kW) | 1.5 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 24 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 40 | 30 | 0
Efficiency |  | (%) | Volt.(v) | 220 | Current(A) | 11.7 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 73 | M/T Maker | WILO | Turbin | 15 | 13
Item No. |  |  | Serial No. |  | Inspector | Lee.J.K | Run (Hr) | B/R (℃) | Test Date
Model | PBI-802MA |  | Customer |  |  |  | 2 | 33
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Data (hidden)
No. | Model | Capa.(ℓ/min.) | Head(m) | Power Supply | Output | Disharge | Pole | RPM | Impeller Type | Suction | Casing Mat'l | Impeller Mat'l | Shaft Mat'l | Flange Mat'l | Capa1 | Capa2 | Capa3 | Capa4 | Capa5 | Head1 | Head2 | Head3 | Head4 | Head5 | SP1 | SP2 | SP3 | SP4 | SP5 | Eff1 | Eff2 | Eff3 | Eff4 | Eff5 | 380V Amp.
1 | PU-756M | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
2 | PW-K130MA | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
3 | PW-409MA | 32(at Ht 12m) | 30 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.1 | 16.7 | 28.5 | 38 | 55 | 46 | 36 | 21 | 9 | 0.6 | 0.55 | 0.47 | 0.37 | 0.3 | 0 | 11.12 | 20.82 | 26.38 | 18.59 | 8
4 | PW-405M | 40(at Ht 12m) | 36 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 10 | 31 | 41 | 46 | 53 | 46 | 26 | 16 | 9.5 | 0.73 | 0.65 | 0.46 | 0.39 | 0.34 | 0 | 11.48 | 28.68 | 27.55 | 20.94 | 8
5 | PW-804MA | 45(at Ht 12m) | 33 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 15 | 32 | 46 | 50 | 74 | 56 | 34 | 16 | 12 | 0.99 | 0.85 | 0.67 | 0.54 | 0.52 | 0 | 16.14 | 26.51 | 22.15 | 18.88 | 8