## Datasheet
PUMP DATA SHEET
| Model | PBI-LD402MA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Clean Water | Flow | 200 | ℓ/min (Ht=20m) | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | - | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 32 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 32 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 52 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 2 Stage | Rated Power | 0.75*2 | W | Pump | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Bed | SS40
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Valve & etc. | STS304
16 | Bore | Size(Dia) | Rating | Face | Position | Manifold | STS304
17 | Suction | 50A | 10K | □ FF, □ RF | □End □Top □Side
18 | Discharge | 50A | 10K | □ FF, □ RF | □Top, □Side
19 | Impeller Type | Closed | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | ■ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath | ■ N.A | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6304ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Inverter motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 0.75kW * 2 |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type | MG12/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 51 Kg

## Outline drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Booster System
MODEL |  | PBI-LD402MA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of Booster System

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
Cls. | Part Name | Specification |  | Quantity | Remarks
1 | Motor Assembly | 3phase 220V 60Hz |  | 1
2 | Vibration protector | ABS(HI-100) |  | 1
3 | Fan | PBT(GP-2200) |  | 1
4 | Fan Cover | SCP or ABS(HI-100) |  | 1
5 | Base Plate | SCP |  | 1
6 | Casing | STS304 |  | 1
7 | Drain Plug | STS316L |  | 1
8 | Priming Plug | STS316L |  | 1
9 | Union Assembly | STS304 |  | 1
10 | Check Valve | STS304 |  | 1
11 | 3Way Nipple | STS304 |  | 1
12 | Pressure Tank | SCP/Rubber |  | 1
13 | Pressure Gauge | 15bar |  | 1
14 | Inverter Cover | ABS |  | 1
15 | Inverter Assembly | 1phase 220V 60Hz |  | 1
16 | Inverter Base | ABS |  | 1
17 | Transmitter | 16bar |  | 1
18 | Power Cord | PNCT 3C |  | 1
19 | Discharge manifold | STS304 |  | 1
20 | Suction manifold | STS304 |  | 1
|  |  | TYPE |  | Booster System
|  |  | MODEL |  | PBI-LD402MA
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of PBI-LD Model
2
9
10
11
12
13
17
18
7
1
3
4
5
6
14
15
16
19
20

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA | [10 empty] | Q1 | Q2 | Q = ?
Capacity | (㎥/min) | 0 | 0.12 | 0.19 | 0.22 | 0.25 | 0.27 | 0.29 | 0.325 | 0.29 | 0.325 | 0.4 | 0.288
Dis. Head | (m) | 32.1 | 27.1 | 21.8 | 18.8 | 15.3 | 12.2 | 9.2 | 3.1 | 9.2 | 3.1 | #N/A | #N/A
Suc. Head | (m) | 0 | -1.2 | -1 | -1 | -0.8 | -0.7 | -0.6 | -0.5 | -0.6 | -0.5 | #N/A | #N/A
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A
Total Head | (m) | 33.3 | 27.1 | 22 | 19 | 15.7 | 12.7 | 9.8 | 3.8 | 9.8 | 3.8 | #N/A | #N/A
Water Power | (kW) | 0 | 0.53008 | 0.68134 | 0.68134 | 0.63977 | 0.55893 | 0.46325 | 0.20131 | 0.46325 | 0.20131 | #N/A | #N/A
Shaft Power | (kW) | 0.55918 | 1.1107 | 1.3635 | 1.4324 | 1.4707 | 1.486 | 1.4937 | 1.4631 | 1.4937 | 1.4631 | #N/A | #N/A
Pump Eff. | (%) | 0 | 47.7245 | 49.9707 | 47.5657 | 43.5008 | 37.6118 | 31.0133 | 13.7592 | 31.0133 | 13.7592 | #N/A | #N/A
Speed | (rpm) | 3514 | 3421 | 3371 | 3356 | 3334 | 3329 | 3328 | 3331 | 3328 | 3331 | #N/A | #N/A
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | #N/A | #N/A
Current | (A) | 5.51 | 10.06 | 11.95 | 12.5 | 12.89 | 13.02 | 13.03 | 12.8 | 13.03 | 12.8 | #N/A | #N/A
Motor Input | (kW) | 0.73 | 1.45 | 1.78 | 1.87 | 1.92 | 1.94 | 1.95 | 1.91 | 1.95 | 1.91 | #N/A | #N/A
Motor Eff. | (%) | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | #N/A | #N/A
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Inverter Motor Specification |  |  |  | Test Condition
Capacity | 0.134 | (㎥/min) | Phase(Φ) | 1 | Output(kW) | 0.75*2 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 20 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 50 | 50 | 1.2
Efficiency | 40 | (%) | Volt.(v) | 220 | Current(A) | 2.96*2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 76.6 | M/T Maker | WILO | Magnetic | 16 | 15
Item No. | 2대운전 |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PBI-LD402MA |  | Customer |  |  |  | 2 |  | 2014.01.16
Checked By |  |  |  |  | Approved By
Vacuum | mmhg
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0.87 | 0.97 | 1.16 | 1.88 | 3.1 | 2.17 | 2.79 | 5.06
Vacuum | mmhg | 64.0076 | 71.3648 | 85.3435 | 138.3154 | 228.0732 | 159.6512 | 205.2659 | 372.2743
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification