## Datasheet
PUMP DATA SHEET
| Model | PBI-T406UA | Title |  |  | Sheet No. | 1
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Clean Water | Flow / Pump | 270 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | - | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 70 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 70 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 50 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 2.2 | W | Pump | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Control Panel | SCP1
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Bed | SS40
16 | Bore | Size(Dia) | Rating | Face | Position | Valve & etc. | STS304
17 | Suction | 65A | 10K | □ FF, ■ RF | □End □Top □Side | Manifold | STS304
18 | Discharge | 65A | 10K | □ FF, ■ RF | □Top, □Side
19 | Impeller Type | Closed | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | ■ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath | ■ N.A | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6305 | Thrust Bearing | 6205 | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 2.2kW * 3 |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type | MG12/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | Kg

## Outline drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Booster System
MODEL |  | PBI-T406UA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of Booster System

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Booster System
MODEL |  | PBI-T406UA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of Booster System

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.1 | 0.16 | 0.21 | 0.31 | 0.4 | 0.47 | 0.53
Dis. Head | (m) | 98 | 93 | 88 | 82 | 68 | 50 | 31 | 11.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 98 | 93 | 88 | 82 | 68 | 50 | 31 | 11.5
Water Power | (kW) | 0 | 1.5159 | 2.295 | 2.8069 | 3.436 | 3.26 | 2.3749 | 0.99348
Shaft Power | (kW) | 2.7306 | 4.1442 | 5.0309 | 5.6807 | 6.6201 | 6.9977 | 6.9099 | 6.6289
Pump Eff. | (%) | 0 | 36.5792 | 45.6185 | 49.4108 | 51.903 | 46.587 | 34.3699 | 14.9872
Speed | (rpm) | 3548 | 3521 | 3505 | 3493 | 3469 | 3458 | 3462 | 3468
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.69 | 9.4 | 10.67 | 11.65 | 13.15 | 13.76 | 13.56 | 13.13
Motor Input | (kW) | 3.11 | 4.72 | 5.73 | 6.47 | 7.54 | 7.97 | 7.87 | 7.55
Motor Eff. | (%) | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.27 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 2.2*3 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 70 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 65 | 65 | 0
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 5.1*3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 87.8 | M/T Maker | WILO | Turbin | 16 | 14
Item No. | 3대운전 |  | Serial No. | X1 | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PBI-T406UA |  | Customer |  |  |  | 2 |  | 2009.11.30
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 125 | 130 | 140 | 155 | 165 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 1.699 | 1.767 | 1.9029 | 2.1068 | 2.2427 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0 | 0 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification