## Datasheet
PUMP DATA SHEET
| Model | PBI-W406UA | Title |  |  | Sheet No. | 1
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Clean Water | Flow / Pump | 180 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | - | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 70 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 70 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 45 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 2.2 | W | Pump | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Control Panel | SCP1
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Bed | SS40
16 | Bore | Size(Dia) | Rating | Face | Position | Valve & etc. | STS304
17 | Suction | 50A | 10K | □ FF, ■ RF | □End □Top □Side | Manifold | STS304
18 | Discharge | 50A | 10K | □ FF, ■ RF | □Top, □Side
19 | Impeller Type | Closed | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | ■ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath | ■ N.A | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6305 | Thrust Bearing | 6205 | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 380 | 3 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 2.2kW * 2 |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 14 |  | Set(S)
41 | Mechanical Seal | Type | MG12/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | Kg

## Outline drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Booster System
MODEL |  | PBI-W406UA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PU TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Booster System
MODEL |  | PBI-W406UA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PU TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.3 | 0.33 | 0.35 | 0.3 | 0.33 | 0.35
Dis. Head | (m) | 94.8 | 92 | 85.8 | 77 | 66 | 33 | 20.3 | 11.3 | 33 | 20.3 | 11.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 94.8 | 92 | 85.8 | 77 | 66 | 33 | 20.3 | 11.3 | 33 | 20.3 | 11.3
Water Power | (kW) | 0 | 0.7498 | 1.3985 | 1.8826 | 2.1516 | 1.6137 | 1.0919 | 0.64467 | 1.6137 | 1.0919 | 0.64467
Shaft Power | (kW) | 1.7057 | 2.394 | 3.1549 | 3.7748 | 4.2237 | 4.3776 | 4.3861 | 4.3007 | 4.4802 | 4.3861 | 4.3007
Pump Eff. | (%) | 0 | 31.32 | 44.3284 | 49.8738 | 50.9411 | 36.8627 | 24.8951 | 14.9899 | 36.0185 | 24.8951 | 14.9899
Speed | (rpm) | 3559 | 3543 | 3522 | 3504 | 3490 | 3478 | 3478 | 3482 | 3478 | 3478 | 3482
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.8 | 5.63 | 6.74 | 7.71 | 8.46 | 8.86 | 8.7 | 8.57 | 8.86 | 8.7 | 8.57
Motor Input | (kW) | 1.995 | 2.8 | 3.69 | 4.415 | 4.94 | 5.12 | 5.13 | 5.03 | 5.24 | 5.13 | 5.03
Motor Eff. | (%) | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 85.5
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.24 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 2.2*2 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 30 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 52.5 | 52.5 | 0
Efficiency | 45 | (%) | Volt.(v) | 380 | Current(A) | 5.1*2 | Flow Meter | R.T (℃) | W.T (℃) |  | 0
I/P Out-Dia | 50 | (mm) | Eff.(%) | 85.5 | M/T Maker | WILO | Turbin | 16 | 14
Item No. | 2대운전 |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PBI-W406UA |  | Customer |  |  |  | 2 |  | 2009.11.02
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 125 | 130 | 140 | 155 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 1.699 | 1.767 | 1.9029 | 2.1068 | 2.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67 |  | 21.67 |  | 21.67 |  | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0 | 37.43 | 0 | 37.43 | 0 | 37.43 | 0 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification