## Datasheet
PUMP DATA SHEET
| Model | PUI-S991MA | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Clean Water | Flow | 280 | ℓ/min | NPSHav | mAq
7 | Pumping Temp | AMB. ℃ | Suct.Head | 6 | m | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press | 3 | m | Solid
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 9 | m | Corros.or Erros
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | 40 | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 990 | W | Impeller | STS304
14 | Speed | 3400 rpm | NPSHre |  | mAq | Shaft | SM20C+STS316
15 | Rotation | □ CW, ■ CCW | Column Head |  | m | Casing | PP
16 | Bore | Size(Dia) | Rating | Face | Position | Suct.Flange | PP
17 | Suction | 50A | 10K | □ FF, □ RF | □End □Top □Side | Disch.Flange | PP
18 | Discharge | 50A | 10K | □ FF, □ RF | □Top, □Side | Plate | STS304
19 | Impeller Type | Closed | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 4 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | ■ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath | ■ N.A | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | 6202ZZ | Thrust Bearing | 6305ZZ | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 990W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | ■ B | □ E | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | ■Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker | Burgman | Model & Size | Φ 18 |  | Set(S)
41 | Mechanical Seal | Type | MG12/14 | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | Kg

## Sectional(PUI)
Sheet No.
CUSTOMER
ITEM No.
DATE
Cls. | Part Name | Specification |  | Quantity | Remarks
1 | Motor Assembly | 3phase 220V 60Hz |  | 1
2 | Motor Supporter | ABS(HI-100) |  | 1
3 | Fan | PBT(GP-2200) |  | 1
4 | Fan Cover | SCP |  | 1
5 | Base Plate | HDPE |  | 1
6 | Casing | PP |  | 1
7 | Drain Plug | PP |  | 1
8 | Priming Plug | PP |  | 1
9 | Suction flange | STS304 |  | 1
10 | Check Valve | PP |  | 1
11 | Cross Nipple | STS304 |  | 1
12 | Pressure Tank | SCP/Rubber |  | 1
13 | Pressure Gauge | 10bar |  | 1
14 | Inverter Cover | ABS(AF-305F) |  | 1
15 | Inverter Assembly | - |  | 1
16 | Inverter Base | ABS(AF-305F) |  | 1
17 | Transmitter | 16bar |  | 1
18 | Power Cord | PNCT 3C |  | 1
|  |  | TYPE |  | Multistage Horizontal Pump
|  |  | MODEL |  | PUI-S991MA
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of PUI-S991MA
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18

## Dimension(PUI)
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Multistage Horizontal Pump
MODEL |  | PUI-Model
SERVICE
SCALE : N/S
OUTLINE DRAWING
of PUI-Model

## TestReport
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 93.7 | 134 | 192 | 230 | 284 | 334 | 346
Dis. Head | (m) | 29 | 25 | 23 | 19 | 16 | 10 | 4 | 2.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.11358 | 0.23228 | 0.47688 | 0.68432 | 1.0434 | 1.4431 | 1.5487
Total Head | (m) | 29 | 25.1136 | 23.2323 | 19.4769 | 16.6843 | 11.0434 | 5.4431 | 3.6487
Water Power | (㎾) | 0 | 0.38356 | 0.50744 | 0.60955 | 0.6255 | 0.51122 | 0.29633 | 0.20578
Shaft Power | (㎾) | 0.956 | 1.212 | 1.304 | 1.388 | 1.424 | 1.448 | 1.44 | 1.4336
Pump Eff. | (%) | 0 | 31.647 | 38.9141 | 43.9156 | 43.9252 | 35.3053 | 20.5787 | 14.3539
Speed | (rpm) | 3368 | 3325 | 3401 | 3294 | 3286 | 3282 | 3282 | 3283
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.18 | 9.95 | 10.74 | 11.35 | 11.63 | 11.7 | 11.75 | 11.7
Motor Input | (㎾) | 1.195 | 1.515 | 1.63 | 1.735 | 1.78 | 1.81 | 1.8 | 1.792
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 15 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 11.7 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | WILO | Turbin |  | 20
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PUI-S991MA |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification