## Data sheet
ELECTRIC DEEP WELL PUMP DATA SHEET
| Model | PC-601NMA |  |  | Title | ELECTRIC DEEP WELL PUMP
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Water |  |  | Capacity | 34
7 | Pumping Temp. |  | Winter : 0 ℃ |  |  | Disch.Press | 1.1 |  |  |  | kgf/㎠G
8 |  |  | Summer : 40 ℃ |  |  | Suction Haed | 12 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 23 |  | m
10 | Viscosity at Pumping Temp. |  |  | - |  | Liquid pH |  |  | 6~8 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | ■Horizontal □Vertical |  | C.W.L | - | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected | - | % | Impeller |  | NORYL
14 | Speed |  | 3450 | rpm | Rated Power | - | kW | Shaft |  | SM20C+STS410
15 | Rotation Viewde From Driver |  |  | ■cw □ccw | NPSHRe | - | mAq | Casing |  | GC150
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | ALDC8
17 |  | Suction | Φ32 | - | - | - |  | Bracket |  | GC150
18 |  | Discharge | Φ25 | - | - | - |  | Flange |  | GC200
19 | Impeller Type |  | ■Close □Semi-Open □Open |  |  | Single Suction
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | □Yes ■No
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model | -
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Open □Stand □Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow □Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6202ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  |  |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 600 |  | Amperage | - |  | Impeller |  |  | Set(s)
33 | Max. Power at any curve Point | [6 empty] | Shaft |  |  | Set(s)
34 | ACCESSORIES (Supplied by : WILO) | [6 empty] | Sleeve |  |  | Set(s)
35 | ■ Companion Flange | [6 empty] | Bearing |  |  | Set(s)
36 | □ Foundation Bolts & Nuts | [6 empty] | Casing |  |  | Set(s)
37 | □ Mechanical Seal |  | Maker | NEK | Model & Size | Φ15 |  | M/Seal |  |  | Set(s)
38 |  |  | Type | Single seal | Cooler Type | - |  | Name Plate |  |  | Set(s)
39 |  |  | Cooler | □Yes ■No | Cooler Quantity | -
40 | □ Protector |  | □Over Load Protector(O.L.P) ■Thermal Protector(T.P)
41 | □ Chain | [6 empty] | WEIGHT
42 | □ Guide Pipe | [6 empty] | Pump | 31 |  | kg
43 | □ Special Tools | [6 empty] | Guide Rail | - |  | kg
44 | □ Spare Parts | [6 empty] | Total Wt. | 32 |  | kg
45 | ■ JET ASSY
REMARKS

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 34 |  | MOTOR | OUTPUT |  |  |  | W | 600
| DISCHARGE HEAD | m | 11 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø | 32 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | single phase
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | ELECTRIC DEEP WELL
[7 empty] | MODEL |  | PC-601NMA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PC TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | KS | ASTM | DIN |  |  | Q'ty
1 | CASING COVER | GC150 | CLASS NO.25 | GG15 |  |  | 1
2 | IMPELLER | NORYL | - | - |  |  | 1
3 | MECHANICAL SEAL | CERAMIC+CARBON | - | - |  |  | 1
4 | O-RING | NBR | - | - |  |  | 1
5 | GASKET | NBR | - | - |  |  | 2
6 | FLANGE | GC200 | CLASS NO.30 | GG20 |  |  | 2
7 | GUIDE VANE | NORYL | - | - |  |  | 1
8 | MOTOR | - | - | - |  |  | 1
9 | CONTROLL VALVE | CR(Rubber) | - | - |  |  | 1
10 | NORMAL TANK | SCP3 | - | - |  |  | 1
11 | PRESSURE SWITCH | - | - | - |  |  | 1
12 | CAPACITOR COVER | ABS | - | - |  |  | 1
|  |  |  | TYPE |  | ELECTRIC DEEP WELL PUMP
|  |  |  | MODEL |  | PC-601NMA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PC TYPE

## Peformance Curve
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 2.7 | 5.9 | 11.8 | 14.5 | 14.7 | 14.7 | 14.8
Dis. Head | (m) | 38 | 33 | 28 | 20 | 16 | 11 | 5 | 0
Suc. Head | (m) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Speed Head | (m) | 0 | 0.00026904 | 0.0012847 | 0.0051387 | 0.0077594 | 0.0079749 | 0.0079749 | 0.0080838
Total Head | (m) | 56 | 51.0003 | 46.0013 | 38.0051 | 34.0078 | 29.008 | 23.008 | 18.0081
Water Power | (㎾) | 0 | 0.022445 | 0.044239 | 0.073099 | 0.080377 | 0.069506 | 0.055129 | 0.043443
Shaft Power | (㎾) | 0.5358 | 0.534 | 0.5334 | 0.5328 | 0.5316 | 0.5394 | 0.5352 | 0.5286
Pump Eff. | (%) | 0 | 4.2032 | 8.2939 | 13.7198 | 15.1199 | 12.8858 | 10.3007 | 8.2184
Speed | (rpm) | 3442 | 3442 | 3441 | 3436 | 3432 | 3428 | 3430 | 3430
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 4.27 | 4.25 | 4.24 | 4.22 | 4.22 | 4.28 | 4.24 | 4.21
Motor Input | (㎾) | 0.893 | 0.89 | 0.889 | 0.888 | 0.886 | 0.899 | 0.892 | 0.881
Motor Eff. | (%) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 10 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 32 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 60 | Maker | WILO | Turbin | 26 | 24
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PC-601NMA |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 882.864 | 882.864 | 882.864 | 882.864 | 882.864 | 882.864 | 882.864 | 882.864
Suc. Head | m | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Suc. Head | m | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Vacuum | mmhg | 882.864 | 882.864 | 882.864 | 882.864 | 882.864 | 882.864 | 882.864 | 882.864
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification