## Summary
CUSTOMER
ITEM No.
DATE
GENERAL SUMMARY OF SUBMERSIBLE PUMP
for SUMP
|  |  | Model Designation |  | PD-3701I + AD-80
| SPECIFICATION | Pump Type |  |  |  | General Drainage
|  | Output(P2) |  |  |  | 3.7 kW(5HP)
|  | Power Supply |  |  |  |  | 1 | I
|  | Discharge Bore |  |  |  |  | 1 | AD-80
|  | Standard Hydraulic Duty |  |  |  | 0.5m3/min - 21m
|  | Requested Hydraulic Duty |  | Capacity | m3/min | Total Head |  |  | m
| MATERIAL | Casing |  |  |  | GC200
|  | Impeller |  |  |  | GCD700
|  | Suction Cover |  |  |  | GCD500
|  | Shaft |  |  |  | STS410
|  | Connector |  |  |  | GC200
|  | Slide |  |  |  | GC200
|  | Mechanical Seal |  |  |  | Lower : SiC + SiC
Upper : Ceramic + Carbon
| ACCESS -ARY | Motor Protector |  |  |  | Installed
|  | Adapter(Auto Guide Rail System) |  |  |  |  | TRUE
Revision 2.3(Nov. 2012)
*Don't modify anything except yellow marked area. | [6 empty] | TYPE |  | General Drainage
* All data in this file can be changed without prior notice. | [6 empty] | MODEL |  | PD-3701I + AD-80
SERVICE
[7 empty] | SCALE |  | N/S
Supply
80mm
65mm

## Data Sheet
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-3701I + AD-80 |  |  | Title | Submersible Pump for Sump with Adapter
1 | Customer |  |  |  |  | Agent Name
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity |  |  |  |  | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity | 0.5 m3/min |  | 30 m3/hr
7 | Pumping Temperature |  | Winter : -5 ℃ |  |  | Disch.Press | - |  |  |  | kgf/cm2G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 21 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 |  | Shut-off Head | 34 |  |  |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH | 6.5~9 |  |  |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □ Horizontal ■ Vertical |  |  |  |  | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | C.W.L | 592 | mm | Impeller |  | GCD700
14 | Speed |  | 3450 | rpm | Eff. Expected | - | % | Shaft |  | STS410
15 | Rotation Viewed From Driver |  |  | ■ Clockwise □ Countercolckwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC200
17 |  | Suction | - | - | □ FF □ RF | - |  | Head Cover |  | GC200
18 |  | Discharge | 80mm | KS 10K | □ FF ■ RF | □ Top ■ Side |  | Cable |  | 60245 KS IEC 57
19 | Impeller Type |  | □ Close ■ Semi-Open □ Open |  |  | Single Suction |  | Mechanical Seal |  | SiC+SiC/Ceramic+Carbon
20 | Flow Direction |  | ■ Radial □ Mixed □ Axial |  | Oil Seal | ■ Yes □ No |  | Connector |  | GC200
21 | Shaft Seal |  | ■ Mech. Seal □ Gland |  | Shaft Sleeve | □ Yes ■ No |  | Suction Cover |  | GCD500
22 | Adapter |  | ■ Yes □ No |  | Adapter Model | AD-80 |  | Slide |  | GC200
23 | Discharge Type |  | □ Hose Connection ■ Flange Conection |  |  |  |  | Flange |  | SM45C
24 | Structure of Inlet |  | □ Open □ Stand ■ Strainer |  |  |  |  | HYDROSTATIC
25 | Structure of Outlet |  | □ PF Tap Flange ■ Welding Flange □ Hose |  |  |  |  | Casing | kgf/cm2 |  | min.
26 | Bearings |  | Upper : | 6304zz | Lower : | 6307zz |  | Frame | kgf/cm2 |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Three Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | D.O.L. |  | Power Supply | 3Phase,380V,60Hz |  | Hydrostatic | □Yes ■No |  | □Yes ■No
31 | Pole & Speed |  | 2pole | 3600rpm | Insulation Class | F |  | SPARE PARTS
32 | Output |  | 3.7kW | 5HP | Amperage | 8.1 A |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □ Thermal Protector(T.P) |  |  |  |  | Casing |  |  | Set(s)
34 | SEAL PART | [6 empty] | M/Seal |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED560-025 |  | Frame Ass'y |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Rotor Ass'y |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 1100 cc |  | Bearing |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Oil Seal |  |  | Set(s)
39 | ■ Companion Flange | [6 empty] | Name Plate |  |  | Set(s)
40 | ■ Chain | [9 empty] | Set(s)
41 | □ Hose Coupling □ Flange Coupling | [9 empty] | Set(s)
42 | □ Foundation Bolts & Nuts | [6 empty] | WEIGHT
43 | □ Guide Pipe | [6 empty] | Pump | 68 |  | kg
44 | □ Special Tools | [6 empty] | Adapter | 40 |  | kg
45 | □ Spare Parts | [6 empty] | Total | 108 |  | kg
REMARKS
| * The above data can be changed without prior notice. | [6 empty] | Revision 2.3(Nov. 2012)

## Pump+Adapter Outline
CUSTOMER
ITEM No.
DATE
OUTLINE DRAWING OF SUBMERSIBLE PUMP
for SUMP with ADAPTER
SPECIFICATION
| Discharge Bore |  |  |  | mm | 80
| MOTOR | Output(P2) |  |  | kW | 3.7
|  | Voltage |  |  | V | 380
|  | Frequency |  |  | Hz | 60
|  | No. of Revolution |  |  | rpm | 3450
|  | Type |  | Three Phase Induction Motor |  | #REF!
(Submersible)
a | b | c | d | e | f | g | h | j | k | L | m | n
180 | 100 | 120 | 150 | 330 | 105 | 105 | 64 | 242 | 592 | 417 | 659 | 80
p | q | r | s | t | (u) | (v) |  |  |  | Revision 2.3(Nov. 2012)
50A | 80 | 160 | 548 | 262 | 600 | 450 |  | TYPE |  | General Drainage | #REF! | #REF!
* C.W.L : Continuous Running Water Level | [7 empty] | MODEL |  | PD-3701I + AD-80
* L.W.L : Least Running Water Level | [7 empty] | SERVICE
* #:Not contained
* All Dimensions in millimeters.
* The above figure and data can be changed without prior notice. | [7 empty] | SCALE |  | N/S

## Pump+Adapter Section
CUSTOMER
ITEM No.
DATE
SECTIONAL DRAWING OF SUBMERSIBLE PUMP
for SUMP with ADAPTER
| * The above figure and data can be changed without prior notice. |  |  |  |  | MODEL | PD-3701I + AD-80
Revision 2.3(Nov. 2012)
| No. | Part Name | Material | Q'ty | No. | Part Name | Material | Q'ty
| 1 | Cable Ass'y | 60245 KS IEC 57 | 8m | 11 | Chain | SS400 | 1
| 2 | Frame Ass'y | - | 1 | 12 | Slide | GC200 | 1
| 3 | Rotor Ass'y | - | 1 | 13 | Casing | GC200 | 1
| 4 | Head Cover | GC200 | 1 | 14 | Impeller | GCD700 | 1
| 5 | Upper Bearing | - | 1 | 15 | Guide Ring | STS304 | 2
| 6 | Lower Bearing | - | 1 | 16 | Suction Cover | GCD500 | 1
| 7 | End Bracket | GC200 | 1 | 17 | KEY | SCP1 | 1
| 8 | Motor Ass'y | - | 1 | 18 | Flange | SM45C | 1
| 9 | Mechanical Seal | SiC+SiC/Ceramic+Carbon | 1 | 19 | Connector | GC200 | 1
| 10 | Oil Seal | NBR | 1 | 20 | Guide Holder | SS400 | 1

## Estimated Curve
CUSTOMER
ITEM No.
DATE
ESTIMATED PERFORMANCE CURVE
SUBMERSIBLE PUMP for SUMP
SPECIFICATION
| PUMP | CAPACITY(m3/min) |  |  | 0.5 |  | MOTOR | OUTPUT[kW(HP)] |  |  | 3.7(5)
|  | TOTAL HEAD(m) |  |  | 21 |  |  | VOLTAGE(V) |  |  | 380
|  | SUCTION BORE(mm) |  |  | - |  |  | AMPERAGE(A) |  |  | 8.1 A
|  | DISCHARGE BORE(mm) |  |  | 80 |  |  | FREQUENCY(Hz) |  |  | 60
|  | IMPELLER TYPE |  |  | Semi-Open |  |  | No. OF REVOLUTION |  |  | 3450rpm
|  | LIQUID |  | Drainage Water |  |  |  | TYPE |  | SUBMERSIBLE
Revision 2.3(Nov. 2012)
[9 empty] | TYPE |  | General Drainage
[9 empty] | MODEL |  | PD-3701I
SERVICE
* The above data can be changed without prior notice.
[9 empty] | SCALE |  | N/S
* Don't Modify Below Area!
Pump Data
Capacity(㎥/min) | 0 | 0.09 | 0.18 | 0.3 | 0.45 | 0.6 | 0.65
Total Head(m) | 34 | 33.5 | 32 | 29.5 | 24.5 | 12 | 3.5
Shaft Power(kW) | 2.4255 | 2.6182 | 2.8029 | 3.1563 | 3.341 | 3.3973 | 3.5
Pump Eff.(%) | 0 | 18.7702 | 33.4963 | 45.7036 | 53.7879 | 34.5455 | 10.595

## Data (hidden)
No. | Power Supply | Code | No. | Discharge | Code
1 | 3~380V,60Hz(Standard) | I | 1 | 80mm | AD-65
2 | 3~220V,60Hz | T | 2 | 65mm | AD-80
3 | 3~440V,60Hz | V