## Summary
CUSTOMER
ITEM No.
DATE
GENERAL SUMMARY OF SUBMERSIBLE PUMP
for SUMP
|  |  | Model Designation |  | PDN-5500I + AD-100
| SPECIFICATION | Pump Type |  |  |  | Non-clog
|  | Output(P2) |  |  |  | 5.5 kW(7.5HP)
|  | Power Supply |  |  |  |  | 1 | I
|  | Discharge Bore |  |  |  |  | 1 | AD-100
|  | Standard Hydraulic Duty |  |  |  | 1.0m3/min - 16m
|  | Requested Hydraulic Duty |  | Capacity | m3/min | Total Head |  |  | m
| MATERIAL | Casing |  |  |  | GC200
|  | Impeller |  |  |  | GC200
|  | Stand |  |  |  | GC200
|  | Shaft |  |  |  | STS410
|  | Connector |  |  |  | GC200
|  | Slide |  |  |  | GC200
|  | Mechanical Seal |  |  |  | Lower : SiC + SiC
Upper : Ceramic + Carbon
| ACCESS -ARY | Motor Protector |  |  |  | Installed
|  | Adapter(Auto Guide Rail System) |  |  |  |  | TRUE
Revision 2.2(July 2004)
*Don't modify anything except yellow marked area. | [6 empty] | TYPE |  | Non-clog
* All data in this file can be changed without prior notice. | [6 empty] | MODEL |  | PDN-5500I + AD-100
SERVICE
[7 empty] | SCALE |  | N/S
Supply
100mm
80mm

## Data Sheet
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-5500I + AD-100 |  |  | Title | Submersible Pump for Sump with Adapter
1 | Customer |  |  |  |  | Agent Name
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity |  |  |  |  | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity | 1.0 m3/min |  | 60 m3/hr
7 | Pumping Temperature |  | Winter : -5 ℃ |  |  | Disch.Press | - |  |  |  | kgf/cm2G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 10 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 |  | Shut-off Head | 25 |  |  |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH | 6.5~9 |  |  |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □ Horizontal ■ Vertical |  |  |  |  | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | C.W.L | 723 | mm | Impeller |  | GC200
14 | Speed |  | 1750 | rpm | Eff. Expected | - | % | Shaft |  | STS410
15 | Rotation Viewed From Driver |  |  | ■ Clockwise □ Countercolckwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □ FF □ RF | - |  | Head Cover |  | GC150
18 |  | Discharge | 100mm | KS 10K | □ FF ■ RF | □ Top ■ Side |  | Cable |  | 2RNCT
19 | Impeller Type |  | □ Close ■ Semi-Open □ Open |  |  | Single Suction |  | Mechanical Seal |  | SiC+SiC/Ceramic+Carbon
20 | Flow Direction |  | ■ Radial □ Mixed □ Axial |  | Oil Seal | ■ Yes □ No |  | Connector |  | GC200
21 | Shaft Seal |  | ■ Mech. Seal □ Gland |  | Shaft Sleeve | □ Yes ■ No |  | Suction Cover |  | GC200
22 | Adapter |  | ■ Yes □ No |  | Adapter Model | AD-100 |  | Slide |  | GC200
23 | Discharge Type |  | □ Hose Connection ■ Flange Conection |  |  |  |  | Flange |  | SM45C
24 | Structure of Inlet |  | □ Open ■ Stand □ Strainer |  |  |  |  | HYDROSTATIC
25 | Structure of Outlet |  | □ PF Tap Flange ■ Welding Flange □ Hose |  |  |  |  | Casing | kgf/cm2 |  | min.
26 | Bearings |  | Upper : | 6305zz | Lower : | 6310zz |  | Frame | kgf/cm2 |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | OTIS-LG Elevator Company |  |  | (Items) |  |  | (Witness)
29 | Type |  | Three Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | D.O.L. |  | Power Supply | 3Phase,380V,60Hz |  | Hydrostatic | □Yes ■No |  | □Yes ■No
31 | Pole & Speed |  | 4pole | 1800rpm | Insulation Class | B |  | SPARE PARTS
32 | Output |  | 5.5kW | 7.5HP | Amperage | 13.0 A |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □ Thermal Protector(T.P) |  |  |  |  | Casing |  |  | Set(s)
34 | SEAL PART | [6 empty] | M/Seal |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED560-035 |  | Frame Ass'y |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Rotor Ass'y |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 1070 cc |  | Bearing |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Oil Seal |  |  | Set(s)
39 | ■ Companion Flange | [6 empty] | Name Plate |  |  | Set(s)
40 | ■ Chain | [9 empty] | Set(s)
41 | □ Hose Coupling □ Flange Coupling | [9 empty] | Set(s)
42 | □ Foundation Bolts & Nuts | [6 empty] | WEIGHT
43 | □ Guide Pipe | [6 empty] | Pump | 130 |  | kg
44 | □ Special Tools | [6 empty] | Adapter | 42 |  | kg
45 | □ Spare Parts | [6 empty] | Total | 172 |  | kg
REMARKS
| * The above data can be changed without prior notice. | [6 empty] | Revision 2.2(July 2004)

## Pump+Adapter Outline
CUSTOMER
ITEM No.
DATE
OUTLINE DRAWING OF SUBMERSIBLE PUMP
for SUMP with ADAPTER
SPECIFICATION
| Discharge Bore |  |  |  | mm | 100
| MOTOR | Output(P2) |  |  | kW | 5.5
|  | Voltage |  |  | V | 380
|  | Frequency |  |  | Hz | 60
|  | No. of Revolution |  |  | rpm | 1750 rpm
|  | Type |  | Three Phase Induction Motor |  | #REF!
(Submersible)
a | b | c | d | e | f | g | h | j | k | L | m | n
180 | 100 | 200 | 238 | 330 | 114 | 115 | 69 | 258 | 723 | 468 | 779 | 100
p | q | r | s | t | (u) | (v) |  |  |  | Revision 2.2(July 2004)
50A | 80 | 160 | 661 | 388 | 710 | 570 |  | TYPE |  | Non-clog | #REF! | #REF!
* C.W.L : Continuous Running Water Level | [7 empty] | MODEL |  | PDN-5500I + AD-100
* L.W.L : Least Running Water Level | [7 empty] | SERVICE
* #:Not contained
* All Dimensions in millimeters.
* The above figure and data can be changed without prior notice. | [7 empty] | SCALE |  | N/S

## Pump+Adapter Section
CUSTOMER
ITEM No.
DATE
SECTIONAL DRAWING OF SUBMERSIBLE PUMP
for SUMP with ADAPTER
| * The above figure and data can be changed without prior notice. |  |  |  |  | MODEL | PDN-5500I + AD-100
Revision 2.2(July 2004)
| No. | Part Name | Material | Q'ty | No. | Part Name | Material | Q'ty
| 1 | Cable Ass'y | 2RNCT | 8m | 11 | Oil Seal | NBR | 1
| 2 | Head Cover | GC150 | 1 | 12 | Casing | GC200 | 1
| 3 | Upper Bearing | - | 1 | 13 | Impeller | GC200 | 1
| 4 | Frame | GC150 | 1 | 14 | Stand | GC200 | 1
| 5 | Lower Bearing | - | 1 | 15 | Impeller Washer | STS304 | 1
| 6 | End Bracket | GC150 | 1 | 16 | Guide Holder | SS400 | 1
| 7 | Motor Ass'y | - | 1 | 17 | Slide | GC200 | 1
| 8 | Chain | SS400 | 1 | 18 | Guide Ring | STS304 | 2
| 9 | Mechanical Seal | SiC+SiC/Ceramic+Carbon | 1 | 19 | Flange | SM45C | 1
| 10 | Oil | T-#32 | 1070cc | 20 | Connector | GC200 | 1

## Estimated Curve
CUSTOMER
ITEM No.
DATE
ESTIMATED PERFORMANCE CURVE
SUBMERSIBLE PUMP for SUMP
SPECIFICATION
| PUMP | CAPACITY(m3/min) |  |  | 1.0 |  | MOTOR | OUTPUT[kW(HP)] |  |  | 5.5(7.5)
|  | TOTAL HEAD(m) |  |  | 16 |  |  | VOLTAGE(V) |  |  | 380
|  | SUCTION BORE(mm) |  |  | - |  |  | AMPERAGE(A) |  |  | 13.0 A
|  | DISCHARGE BORE(mm) |  |  | 100 |  |  | FREQUENCY(Hz) |  |  | 60
|  | IMPELLER TYPE |  |  | Single Channel |  |  | No. OF REVOLUTION |  |  | 1750 rpm
|  | LIQUID |  | Drainage Water |  |  |  | TYPE |  | SUBMERSIBLE
Revision 2.2(July 2004)
[9 empty] | TYPE |  | Non-clog
[9 empty] | MODEL |  | PDN-5500I
SERVICE
* The above data can be changed without prior notice.
[9 empty] | SCALE |  | N/S
* Don't Modify Below Area!
Pump Data
Capacity(㎥/min) | 0 | 0.4 | 0.7 | 1 | 1.3 | 1.6 | 2.04
Total Head(m) | 25.2 | 21.44 | 18.81 | 15.93 | 12.89 | 10.09 | 4.96
Shaft Power(kW) | 4 | 4.47 | 4.74 | 5.11 | 5.38 | 5.67 | 5.8
Pump Eff.(%) | 0 | 31.2727 | 45.2789 | 50.8139 | 50.7693 | 46.4104 | 28.4362

## Data (hidden)
No. | Power Supply | Code | No. | Discharge | Code
1 | 3~380V,60Hz(Standard) | I | 1 | 80mm | AD-80
2 | 3~220V,60Hz | T | 2 | 100mm | AD-100
3 | 3~440V,60Hz | V