## Summary
CUSTOMER
ITEM No.
DATE
GENERAL SUMMARY OF SUBMERSIBLE PUMP
for SUMP
|  |  | Model Designation |  |  | PDN-7500I
| SPECIFICATION | Pump Type |  |  |  |  | Non-clog
|  | Output(P2) |  |  |  |  | 7.5 kW(10HP)
|  | Power Supply | [5 empty] | 1 | I
|  | Discharge Bore |  |  |  |  | PF 4"(100mm)
|  | Standard Hydraulic Duty |  |  |  |  | 1.4m3/min - 17m
|  | Requested Hydraulic Duty |  | Capacity | 0.9 | m3/min | Total Head |  | 22 | m
| MATERIAL | Casing |  |  |  |  | GC200
|  | Impeller |  |  |  |  | GC200
|  | Stand |  |  |  |  | GC200
|  | Shaft |  |  |  |  | STS410
|  | Frame |  |  |  |  | GC150
|  | Head Cover |  |  |  |  | GC150
|  | Mechanical Seal |  |  |  |  | Lower : SiC + SiC
Upper : Ceramic + Carbon
| ACCESS -ARY | Motor Protector |  |  |  |  | Installed
|  | Adapter(Auto Guide Rail System) | [5 empty] | FALSE
Revision 2.2(April 2004)
*Don't modify anything except yellow marked area. | [7 empty] | TYPE |  | Non-clog
* All data in this file can be changed without prior notice. | [7 empty] | MODEL |  | PDN-7500I
SERVICE
[8 empty] | SCALE |  | N/S
n/a

## Data Sheet
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-7500I |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent Name
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity |  |  |  |  | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity | 0.9 m3/min |  | 54 m3/hr
7 | Pumping Temperature |  | Winter : -5 ℃ |  |  | Disch.Press | - |  |  |  | kgf/cm2G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 22 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 |  | Shut-off Head | 30 |  |  |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH | 6.5~9 |  |  |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □ Horizontal ■ Vertical |  |  |  |  | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | C.W.L | 654 | mm | Impeller |  | GC200
14 | Speed |  | 1750 | rpm | Eff. Expected | - | % | Shaft |  | STS410
15 | Rotation Viewed From Driver |  |  | ■ Clockwise □ Countercolckwise |  |  |  | Mechanical Seal |  | SiC+SiC/Ceramic+Carbon
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Casing |  | GC200
17 |  | Suction | - | - | □ FF □ RF | - |  | Stand |  | GC200
18 |  | Discharge | PF 4"(100mm) | - | □ FF ■ RF | □ Top ■ Side |  | Frame |  | GC150
19 | Impeller Type |  | □ Close ■ Semi-Open □ Open |  |  | Single Suction |  | Head Cover |  | GC150
20 | Flow Direction |  | ■ Radial □ Mixed □ Axial |  | Oil Seal | ■ Yes □ No |  | Stand |  | GC200
21 | Shaft Seal |  | ■ Mech. Seal □ Gland |  | Shaft Sleeve | □ Yes ■ No |  | Flange |  | GC200
22 | Adapter |  | □ Yes ■ No |  | Adapter Model | N/A |  | Elbow |  | GC200
23 | Discharge Type |  | □ Hose Connection ■ Flange Conection |  |  |  |  | Cable |  | 2RNCT
24 | Structure of Inlet |  | □ Open ■ Stand □ Strainer |  |  |  |  | HYDROSTATIC
25 | Structure of Outlet |  | ■ PF Tap Flange □ Welding Flange □ Hose |  |  |  |  | Casing | kgf/cm2 |  | min.
26 | Bearings |  | Upper : | 6305zz | Lower : | 6310zz |  | Frame | kgf/cm2 |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | OTIS-LG Elevator Company |  |  | (Items) |  |  | (Witness)
29 | Type |  | Three Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | D.O.L. |  | Power Supply | 3Phase,380V,60Hz |  | Hydrostatic | □Yes ■No |  | □Yes ■No
31 | Pole & Speed |  | 4pole | 1800rpm | Insulation Class | B |  | SPARE PARTS
32 | Output |  | 7.5kW | 10HP | Amperage | 17.0 A |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □ Thermal Protector(T.P) |  |  |  |  | Casing |  |  | Set(s)
34 | SEAL PARTS | [6 empty] | M/Seal |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED560-035 |  | Frame Ass'y |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Rotor Ass'y |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 1070 cc |  | Bearing |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Oil Seal |  |  | Set(s)
39 | ■ Companion Flange | [6 empty] | Name Plate |  |  | Set(s)
40 | □ Chain | [9 empty] | Set(s)
41 | □ Hose Coupling □ Flange Coupling | [9 empty] | Set(s)
42 | □ Foundation Bolts & Nuts | [6 empty] | WEIGHT
43 | □ Guide Pipe | [6 empty] | Pump | 131 |  | kg
44 | □ Special Tools | [6 empty] | Adapter | - |  | kg
45 | □ Spare Parts | [6 empty] | Total | 131 |  | kg
REMARKS
| * The above data can be changed without prior notice. | [6 empty] | Revision 2.2(April 2004)

## Pump Outline
CUSTOMER
ITEM No.
DATE
OUTLINE DRAWING OF SUBMERSIBLE PUMP
for SUMP
SPECIFICATION
| Discharge Bore |  |  |  | "(mm) | PF 4"(100mm)
| MOTOR | Output(P2) |  |  | kW | 7.5
|  | Voltage |  |  | V | 380
|  | Frequency |  |  | Hz | 60
|  | No. of Revolution |  |  | rpm | 1750 rpm
|  | Type |  | Three Phase Induction Motor |  | #REF!
(Submersible)
|  | a | b | c | d | e | f | g | h
|  | 636 | 337 | 388 | 271 | 189 | 654 | 710 | PF 4"(100mm)
Revision 2.2(April 2004)
|  | (Submersible) g: TYPE | Non-clog | #REF! | #REF!
* C.W.L : Continuous Running Water Level |  | (Submersible) g: MODEL | PDN-7500I | #REF! | #REF!
* L.W.L : Least Running Water Level |  | (Submersible) g: SERVICE
* All Dimensions in millimeters.
* The above figure and data can be changed without prior notice.
|  | (Submersible) g: SCALE | N/S

## Pump Section
CUSTOMER
ITEM No.
DATE
SECTIONAL DRAWING OF SUBMERSIBLE PUMP
for SUMP
| * The above figure and data can be changed without prior notice. |  |  |  |  | MODEL | PDN-7500I
Revision 2.2(April 2004)
| No. | Part Name | Material | Q'ty | No. | Part Name | Material | Q'ty
| 1 | Cable Ass'y | 2RNCT | 8m | 11 | Oil | T-#32 | 1070cc
| 2 | Rotor Ass'y | - | 1 | 12 | Oil Seal | NBR | 1
| 3 | Stator Ass'y | - | 1 | 13 | O-Ring | NBR | 1
| 4 | Head Cover | GC150 | 1 | 14 | Casing | GC200 | 1
| 5 | Upper Bearing | - | 1 | 15 | Impeller | GC200 | 1
| 6 | Frame | GC150 | 1 | 16 | Impeller Washer | STS304 | 1
| 7 | Lower Bearing | - | 1 | 17 | Impeller Bolt | STS304 | 1
| 8 | End Bracket | GC150 | 1 | 18 | Stand | GC200 | 1
| 9 | Motor Ass'y | - | 1 | 19 | Flange | GC200 | 1
| 10 | Mechanical Seal | SiC+SiC/Ceramic+Carbon | 1 | 20 | Elbow | GC200 | 1

## Estimated Curve
CUSTOMER
ITEM No.
DATE
ESTIMATED PERFORMANCE CURVE
SUBMERSIBLE PUMP for SUMP
SPECIFICATION
| PUMP | CAPACITY(m3/min) |  |  | 0.9 |  | MOTOR | OUTPUT[kW(HP)] |  |  | 7.5(10)
|  | TOTAL HEAD(m) |  |  | 22 |  |  | VOLTAGE(V) |  |  | 380
|  | SUCTION BORE |  |  | - |  |  | AMPERAGE(A) |  |  | 17.0 A
|  | DISCHARGE BORE |  |  | PF 4"(100mm) |  |  | FREQUENCY(Hz) |  |  | 60
|  | IMPELLER TYPE |  |  | Single Channel |  |  | No. OF REVOLUTION |  |  | 1750 rpm
|  | LIQUID |  | Drainage Water |  |  |  | TYPE |  | SUBMERSIBLE
Revision 2.2(April 2004)
[9 empty] | TYPE |  | Non-clog
[9 empty] | MODEL |  | PDN-7500I
SERVICE
* The above data can be changed without prior notice.
[9 empty] | SCALE |  | N/S
* Don't Modify Below Area!
Pump Data
Capacity(㎥/min) | 0 | 0.4 | 0.8 | 1.4 | 1.9 | 2.29
Total Head(m) | 30.5 | 27 | 23.5 | 17 | 10.5 | 6.4
Shaft Power(kW) | 5.6 | 6.3 | 6.9 | 7.6 | 7.9 | 8.3
Pump Eff.(%) | 0 | 27.9429 | 44.4116 | 51.0447 | 41.1627 | 28.7823

## Data (hidden)
No. | Power Supply | Code
1 | 3~380V,60Hz(Standard) | I
2 | 3~220V,60Hz | T
3 | 3~440V,60Hz | V