## Datasheet(DLV-270MA)
DRAIN PACKAGE DATA SHEET
| Model | DLV-270MA |  |  | Title | Drain Package for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 145 |  | 8700
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.3 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 3 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 9 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 266 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3300 | rpm | Rated Power | 0.3 | kW | Shaft |  | SM20C+STS316 or STS316
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150 or 200
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC200
18 |  | Discharge | Φ32, 1¼" | - | □FF □RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Oil Case |  | GC150
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Lift Case |  | LLDPE
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Lift Cover |  | LLDPE
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3300 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.3 |  | Input | 400 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-012 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 140 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Gasket For Outline
40 | ■ Gasket For Inine
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 14.5 |  | kg
44 | □ Spare Parts | [6 empty] | Drain Package | 6.5 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 21 |  | kg
REMARKS

## Outline Drawing(DLV-270MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 100(Ht=6m) |  | MOTOR | OUTPUT |  |  |  | W | 300
| TOTAL HEAD | m | 9 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 40 (32) |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | SEMI OPEN
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | DRAIN PACKAGE
[7 empty] | MODEL |  | DLV-270MA
SERVICE
[7 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of DLV TYPE

## Sectional Drawing(DLV-270MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | CABLE ASS'Y | 2PNCT | - | - | 1 | 13 | O-RING |  |  | NBR |  | - | - | 1
2 | HEAD COVER | GC200 | Class No 30 | GG20 | 1 | 14 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
3 | GASKET COVER | NBR | - | - | 1 | 15 | IMPELLER |  |  | GC200 |  | Class No 30 | GG20 | 1
4 | CAPACITOR | 14㎌ | - | - | 1 | 16 | PIPE ASSY |  |  | - |  | - | - | 1
5 | ROTOR ASS'Y | - | - | - | 1 | 17 | GASKET, PIPE |  |  | - |  | - | - | 1
6 | FRAME ASS'Y | - | - | - | 1 | 18 | GASKET,PIPE(Ф40) |  |  | - |  | - | - | 1
7 | MOTOR ASS'Y | - | - | - | 1 | 19 | COVER |  |  | LLDPE |  | - | - | 1
8 | OIL SEAL | NBR709 | - | - | 1 | 20 | FASTENER |  |  | STS |  | - | - | 1
9 | MECHANICAL SEAL | Cera+Sic | - | - | 1 | 21 | CASE |  |  | LLDPE |  | - | - | 1
10 | SEAL OIL | NBR709 | - | - | 1 | 22 | CABLE HOLDER |  |  | - |  | - | - | 1
11 | O-RING | NBR | - | - | 1 | 23 | BAND |  |  | - |  | - | - | 1
12 | OIL CASE | GC150 | Class No 25 | GG15 |  | 24 | FLOAT SWITCH |  |  | - |  | - | - | 1
[8 empty] | TYPE |  | DRAIN PACKAGE
[8 empty] | MODEL |  | DLV-270MA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of DLV TYPE

## Test Report(DLV-270MA)
DRAIN PACKAGE TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 35 | 101 | 143 | 161 | 175 | 194 | 208
Dis. Head | (m) | 9.8 | 9 | 7 | 5 | 4 | 3 | 2 | 1.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.026841 | 0.22351 | 0.44806 | 0.56795 | 0.67102 | 0.82464 | 0.94795
Total Head | (m) | 9.8 | 9.0268 | 7.2235 | 5.4481 | 4.568 | 3.671 | 2.8246 | 2.248
Water Power | (㎾) | 0 | 0.051498 | 0.11892 | 0.12699 | 0.11988 | 0.10472 | 0.089321 | 0.076215
Shaft Power | (㎾) | 0.20007 | 0.22422 | 0.25802 | 0.27941 | 0.29252 | 0.30149 | 0.30701 | 0.31459
Pump Eff. | (%) | 0 | 22.9679 | 46.0893 | 45.449 | 40.981 | 34.7332 | 29.0942 | 24.2263
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.34 | 1.43 | 1.81 | 1.97 | 2.01 | 2.03 | 2.04 | 2.05
Motor Input | (㎾) | 0.29 | 0.325 | 0.374 | 0.405 | 0.424 | 0.437 | 0.445 | 0.456
Motor Eff. | (%) | 68.99 | 68.99 | 68.99 | 68.99 | 68.99 | 68.99 | 68.99 | 68.99
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 145 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.3 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 3 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.99 | Maker | WILO | Turbin | 20 | 14
Item No. |  |  | Serial No. |  | Inspector | S.K.S | Run (Hr) | B/R (℃) | Test Date
Model | PDV-270MA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288
Suc. Head | m | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Suc. Head | m | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Vacuum | mmhg | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification