## Datasheet(PD-200M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-200M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 130 |  | 7800
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.1 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 1 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 9 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 55 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP
14 | Speed |  | 3450 | rpm | Rated Power | 0.2 | kW | Shaft |  | STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | mPPO
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | mPPO
17 |  | Suction | - | - | □FF □RF | - |  | Hose Coupling |  | PP
18 |  | Discharge | Φ20,25,11/4" | - | □FF □RF | ■Top □Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Impeller |  | mPPO
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Seal Cover |  | mPPO
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | ■Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6200ZZ |  | Lower : 6200ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.2 |  | Input | 360 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Hose Coupling |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | BT PR/AR 10 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 20 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 4.5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 4.5 |  | kg
REMARKS

## Datasheet(PD-200MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-200MA |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 130 |  | 7800
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.1 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 1 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 9 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 55 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP
14 | Speed |  | 3450 | rpm | Rated Power | 0.2 | kW | Shaft |  | STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | mPPO
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | mPPO
17 |  | Suction | - | - | □FF □RF | - |  | Hose Coupling |  | PP
18 |  | Discharge | Φ20,25,11/4" | - | □FF □RF | ■Top □Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Impeller |  | mPPO
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Seal Cover |  | mPPO
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | ■Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6200ZZ |  | Lower : 6200ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.2 |  | Input | 360 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Hose Coupling |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | BT PR/AR 10 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 20 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 5 |  | kg
REMARKS

## Outline Drawing(PD-200M)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 130(Ht=1m) |  | MOTOR | OUTPUT |  |  |  | W | 200
|  | TOTAL HEAD | m | 9 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 32 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PD-200M
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PD TYPE

## Outline Drawing(PD-200MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 130(Ht=1m) |  | MOTOR | OUTPUT |  |  |  | W | 200
|  | TOTAL HEAD | m | 9 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 32 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PD-200MA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PD TYPE

## Sectional Drawing(PD-200M)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | PP | - | - | 1 | 8 | MECHANICAL SEAL |  |  | Car+Cera |  | - | - | 1
2 | MOTOR ASS'Y | - | - | - | 1 | 9 | O-RING |  |  | NBR507 |  | - | - | 2
3 | CABLE ASS'Y | 2PNCT | - | - | 1 | 10 | CASING |  |  | mPPO |  | - | - | 1
4 | GASKET | NBR607 | - | - | 1 | 11 | OIL CASE |  |  | mPPO |  | - | - | 1
5 | TERMINAL | mPPO | - | - | 1 | 12 | IMPELLER |  |  | mPPO |  | - | - | 1
6 | CAPACITOR | - | - | - | 1 | 13 | BODY |  |  | mPPO |  | - | - | 1
7 | OIL SEAL | mPPO | - | - | 2 | 14 | BASE PAD |  |  | NBR607 |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE,NON AUTO)
[8 empty] | MODEL |  | PD-200M
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PD TYPE
1
2
3
4
5
6
7
8
9
10
11
12
13
14

## Sectional Drawing(PD-200MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | PP | - | - | 1 | 8 | MECHANICAL SEAL |  |  | Car+Cera |  | - | - | 1
2 | MOTOR ASS'Y | - | - | - | 1 | 9 | O-RING |  |  | NBR507 |  | - | - | 2
3 | CABLE ASS'Y | 2PNCT | - | - | 1 | 10 | CASING |  |  | mPPO |  | - | - | 1
4 | GASKET | NBR607 | - | - | 1 | 11 | OIL CASE |  |  | mPPO |  | - | - | 1
5 | TERMINAL | mPPO | - | - | 1 | 12 | IMPELLER |  |  | mPPO |  | - | - | 1
6 | CAPACITOR | - | - | - | 1 | 13 | BODY |  |  | mPPO |  | - | - | 1
7 | OIL SEAL | mPPO | - | - | 2 | 14 | BASE PAD |  |  | NBR607 |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE,NON AUTO)
[8 empty] | MODEL |  | PD-200MA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PD TYPE
1
2
3
4
5
6
7
8
9
10
11
12
13
14

## Test Report(PD-200M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 43 | 79 | 117 | 133 | 151
Dis. Head | (m) | 9.3 | 7 | 5 | 3 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.040513 | 0.13675 | 0.29994 | 0.38758 | 0.49959
Total Head | (m) | 9.3 | 7.0405 | 5.1367 | 3.2999 | 2.3876 | 1.4996
Water Power | (㎾) | 0 | 0.049347 | 0.066146 | 0.062933 | 0.05176 | 0.036909
Shaft Power | (㎾) | 0.15925 | 0.1755 | 0.19695 | 0.221 | 0.2288 | 0.23075
Pump Eff. | (%) | 0 | 28.1179 | 33.5851 | 28.4765 | 22.6225 | 15.9954
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.28 | 1.5 | 1.71 | 1.76 | 1.79 | 1.8
Motor Input | (㎾) | 0.245 | 0.27 | 0.303 | 0.34 | 0.352 | 0.355
Motor Eff. | (%) | 65 | 65 | 65 | 65 | 65 | 65
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 1 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 1.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 65 | Maker | WILO | Turbin | 12 | 18
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PD-200M |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PD-200MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 43 | 79 | 117 | 133 | 151
Dis. Head | (m) | 9.3 | 7 | 5 | 3 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.040513 | 0.13675 | 0.29994 | 0.38758 | 0.49959
Total Head | (m) | 9.3 | 7.0405 | 5.1367 | 3.2999 | 2.3876 | 1.4996
Water Power | (㎾) | 0 | 0.049347 | 0.066146 | 0.062933 | 0.05176 | 0.036909
Shaft Power | (㎾) | 0.15925 | 0.1755 | 0.19695 | 0.221 | 0.2288 | 0.23075
Pump Eff. | (%) | 0 | 28.1179 | 33.5851 | 28.4765 | 22.6225 | 15.9954
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.28 | 1.5 | 1.71 | 1.76 | 1.79 | 1.8
Motor Input | (㎾) | 0.245 | 0.27 | 0.303 | 0.34 | 0.352 | 0.355
Motor Eff. | (%) | 65 | 65 | 65 | 65 | 65 | 65
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 1 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 1.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 65 | Maker | WILO | Turbin | 12 | 18
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PD-200MA |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification