## Datasheet(PD-272M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-272M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 140 |  | 8400
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.3 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 3 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 9.5 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 270 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP
14 | Speed |  | 3450 | rpm | Rated Power | 0.3 | kW | Shaft |  | SM20C+STS316L or STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | PP
17 |  | Suction | - | - | □FF □RF | - |  | Hose Coupling |  | pp
18 |  | Discharge | Φ25,32,11/4" | - | □FF □RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Impeller |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Seal Cover |  | PBT
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | ■Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.3 |  | Input | 380 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■Thermal Protector(T.P) |  | Current | 2.0 A |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | ED-560-012 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 55 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 6 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 6 |  | kg
REMARKS

## Datasheet(PD-272MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-272MA |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 140 |  | 8400
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.3 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 3 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 9.5 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 270 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP
14 | Speed |  | 3450 | rpm | Rated Power | 0.3 | kW | Shaft |  | SM20C+STS316L or STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | PP
17 |  | Suction | - | - | □FF □RF | - |  | Hose Coupling |  | pp
18 |  | Discharge | Φ25,32,11/4" | - | □FF □RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Impeller |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Seal Cover |  | PBT
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | ■Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.3 |  | Input | 380 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■Thermal Protector(T.P) |  | Current | 2.0 A |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERMANN | Model & Size | ED-560-012 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 55 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 6 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 6 |  | kg
REMARKS

## Outline Drawing(PD-272MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 140(Ht=3m) |  | MOTOR | OUTPUT |  |  |  | W | 300
|  | TOTAL HEAD | m | 9.5 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 32 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,AUTO)
|  | Water Level | [5 empty] | MODEL |  | PD-272M(A)
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PD TYPE

## Sectional Drawing(PD-272MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | CABLE ASS'Y | 2PNCT | - | - | 1 | 10 | SEAL COVER |  |  | PBT |  | - | - | 1
2 | HANDLE | PP | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+Cera |  | - | - | 1
3 | CAPACITOR | - | - | - | 1 | 12 | SEALING CAP |  |  | NBR610 |  | - | - | 1
4 | BODY | PP | - | - | 1 | 13 | IMPELLER |  |  | PBT |  | - | - | 1
5 | MOTOR ASS'Y | - | - | - | 1 | 14 | STRAINER |  |  | PE |  | - | - | 1
6 | BOLTS | STS304 | 304 | X5CrNi189 | 1 | 15 | CASING |  |  | PP |  | - | - | 1
7 | O-RING | NBR607 | - | - | 1 | 16 | ELBOW |  |  | PP |  | - | - | 1
8 | END BRACKET(A) | Aℓ | - | - | 1 | 17 | O-RING |  |  | NBR607 |  | - | - | 1
9 | OIL SEAL | NBR607 | - | - | 1 | 18 | HOSE COUPLING |  |  | PP |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE,AUTO)
[8 empty] | MODEL |  | PD-272M(A)
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PD TYPE

## Test Report(PD-272M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 62 | 88 | 109 | 123 | 137 | 162 | 175
Dis. Head | (m) | 10.4 | 8 | 7 | 6 | 5 | 4 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.10903 | 0.21965 | 0.337 | 0.42913 | 0.53237 | 0.7444 | 0.86866
Total Head | (m) | 10.4 | 8.109 | 7.2197 | 6.337 | 5.4291 | 4.5324 | 2.7444 | 1.8687
Water Power | (㎾) | 0 | 0.08195 | 0.10356 | 0.11259 | 0.10885 | 0.10121 | 0.072469 | 0.053304
Shaft Power | (㎾) | 0.1589 | 0.217 | 0.2387 | 0.2422 | 0.2604 | 0.2639 | 0.2646 | 0.2646
Pump Eff. | (%) | 0 | 37.7649 | 43.3845 | 46.4861 | 41.8005 | 38.3526 | 27.388 | 20.145
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.13 | 1.43 | 1.6 | 1.7 | 1.73 | 1.74 | 1.75 | 1.75
Motor Input | (㎾) | 0.227 | 0.31 | 0.341 | 0.346 | 0.372 | 0.377 | 0.378 | 0.378
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 140 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.3 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 3 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 30
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 2.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Turbin | 27 | 22
Item No. | N.A |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PD-272M |  | Customer |  |  |  | 1 |  | 08.07.22
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PD-272MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 74 | 101 | 114 | 143 | 156 | 169
Dis. Head | (m) | 10 | 8 | 7 | 6 | 5 | 3 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.070911 | 0.15532 | 0.28935 | 0.36862 | 0.58002 | 0.69028 | 0.81012
Total Head | (m) | 10 | 8.0709 | 7.1553 | 6.2893 | 5.3686 | 3.58 | 2.6903 | 1.8101
Water Power | (㎾) | 0 | 0.065778 | 0.086308 | 0.10354 | 0.09976 | 0.083447 | 0.068408 | 0.049863
Shaft Power | (㎾) | 0.1547 | 0.2002 | 0.2205 | 0.2401 | 0.2457 | 0.2499 | 0.2499 | 0.2506
Pump Eff. | (%) | 0 | 32.8561 | 39.1417 | 43.1243 | 40.6023 | 33.3921 | 27.3743 | 19.8976
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.08 | 1.35 | 1.48 | 1.58 | 1.62 | 1.65 | 1.64 | 1.64
Motor Input | (㎾) | 0.221 | 0.286 | 0.315 | 0.343 | 0.351 | 0.357 | 0.357 | 0.358
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 140 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.3 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 3 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 30
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 2.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Turbin | 27 | 22
Item No. | N.A |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PD-272MA |  | Customer |  |  |  | 1 |  | 08.07.22
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification