## Datasheet(PD-550M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-550M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 145 |  | 8700
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 14 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 86 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP+GF20%
14 | Speed |  | 3450 | rpm | Rated Power | 0.7 | kW | Shaft |  | SM20C + STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | PP+GF30%
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | PP+GF30%
17 |  | Suction | - | - | □FF □RF | - |  | Impeller |  | PBT
18 |  | Discharge | Φ50(2") | - | □FF ■RF | ■Top □Side |  | Cable |  | IEC57x3C
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Oil Case |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Terminal Cover |  | PP+GF30%
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Casing Pad |  | TPE
22 | Adapter |  | □Yes ■No |  | Adapter Model |  |  | Strainer |  | PE
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6302ZZ |  | Lower : 6202ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.7 |  | Input | 950 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Hose Coupling |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | BT PR/AR 10 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 35 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 7.5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 7.5 |  | kg
REMARKS

## Datasheet(PD-550MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-550MA |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 145 |  | 8700
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 14 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 86 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP+GF20%
14 | Speed |  | 3450 | rpm | Rated Power | 0.7 | kW | Shaft |  | SM20C + STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | PP+GF30%
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | PP+GF30%
17 |  | Suction | - | - | □FF □RF | - |  | Impeller |  | PBT
18 |  | Discharge | Φ50(2") | - | □FF ■RF | ■Top □Side |  | Cable |  | IEC57x3C
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Oil Case |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Terminal Cover |  | PP+GF30%
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Casing Pad |  | TPE
22 | Adapter |  | □Yes ■No |  | Adapter Model |  |  | Strainer |  | PE
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6302ZZ |  | Lower : 6202ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.7 |  | Input | 950 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Hose Coupling |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | BT PR/AR 10 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 35 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 8 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 8 |  | kg
REMARKS

## Outline Drawing(PD-550M)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 145(Ht=7m) |  | MOTOR | OUTPUT |  |  |  | W | 700
|  | TOTAL HEAD | m | 14 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PD-550M
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PD TYPE
C.W.L

## Outline Drawing(PD-550MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 145(Ht=7m) |  | MOTOR | OUTPUT |  |  |  | W | 700
|  | TOTAL HEAD | m | 14 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PD-550MA
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PD TYPE
C.W.L

## Sectional Drawing(PD-550M)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | PP | - | - | 1 | 8 | MECHANICAL SEAL |  |  | Car+Cera |  | - | - | 1
2 | MOTOR ASS'Y | - | - | - | 1 | 9 | OIL CASE |  |  | PBT |  | - | - | 1
3 | CABLE ASS'Y | IEC57x3C | - | - | 1 | 10 | CASING |  |  | PP |  | - | - | 1
4 | GASKET | NBR607 | - | - | 1 | 11 | BODY ASSY |  |  | PP |  | - | - | 1
5 | T/COVER | PP | - | - | 1 | 12 | IMPELLER |  |  | PBT |  | - | - | 1
6 | CAPACITOR | - | - | - | 1 | 13 | CASING PAD |  |  | TPE |  | - | - | 1
7 | O-RING | NBR607 | - | - | 2 | 14 | STRAINER |  |  | PE |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE,NON AUTO)
[8 empty] | MODEL |  | PD-550M
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PD TYPE
1
2
3
4
5
6
7
8
9
10
11
12
13

## Sectional Drawing(PD-550MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | PP | - | - | 1 | 8 | MECHANICAL SEAL |  |  | Car+Cera |  | - | - | 1
2 | MOTOR ASS'Y | - | - | - | 1 | 9 | OIL CASE |  |  | PBT |  | - | - | 1
3 | CABLE ASS'Y | IEC57x3C | - | - | 1 | 10 | CASING |  |  | PP |  | - | - | 1
4 | GASKET | NBR607 | - | - | 1 | 11 | BODY ASSY |  |  | PP |  | - | - | 1
5 | T/COVER | PP | - | - | 1 | 12 | IMPELLER |  |  | PBT |  | - | - | 1
6 | CAPACITOR | - | - | - | 1 | 13 | CASING PAD |  |  | TPE |  | - | - | 1
7 | O-RING | NBR607 | - | - | 2 | 14 | STRAINER |  |  | PE |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE,NON AUTO)
[8 empty] | MODEL |  | PD-550MA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PD TYPE
1
2
3
4
5
6
7
8
9
10
11
12
13

## Test Report(PD-550M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 59 | 110 | 159 | 202 | 243 | 268
Dis. Head | (m) | 14.1 | 11 | 9 | 7 | 5 | 3 | 1.8
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012796 | 0.04448 | 0.092934 | 0.15 | 0.21707 | 0.26403
Total Head | (m) | 14.1 | 11.0128 | 9.0445 | 7.0929 | 5.15 | 3.2171 | 2.064
Water Power | (㎾) | 0 | 0.10591 | 0.16217 | 0.18383 | 0.16957 | 0.12742 | 0.090165
Shaft Power | (㎾) | 0.44156 | 0.54416 | 0.6308 | 0.7068 | 0.75316 | 1.0032 | 0.80256
Pump Eff. | (%) | 0 | 19.463 | 25.7082 | 26.0084 | 22.5143 | 12.7018 | 11.2347
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.76 | 3.34 | 3.85 | 4.31 | 4.58 | 4.77 | 4.84
Motor Input | (㎾) | 0.581 | 0.716 | 0.83 | 0.93 | 0.991 | 1.32 | 1.056
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 145 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 7 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 4.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | WILO | Turbin | 16 | 20
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PD-550M |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PD-550MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 59 | 110 | 159 | 202 | 243 | 268
Dis. Head | (m) | 14.1 | 11 | 9 | 7 | 5 | 3 | 1.8
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012796 | 0.04448 | 0.092934 | 0.15 | 0.21707 | 0.26403
Total Head | (m) | 14.1 | 11.0128 | 9.0445 | 7.0929 | 5.15 | 3.2171 | 2.064
Water Power | (㎾) | 0 | 0.10591 | 0.16217 | 0.18383 | 0.16957 | 0.12742 | 0.090165
Shaft Power | (㎾) | 0.44156 | 0.54416 | 0.6308 | 0.7068 | 0.75316 | 1.0032 | 0.80256
Pump Eff. | (%) | 0 | 19.463 | 25.7082 | 26.0084 | 22.5143 | 12.7018 | 11.2347
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.76 | 3.34 | 3.85 | 4.31 | 4.58 | 4.77 | 4.84
Motor Input | (㎾) | 0.581 | 0.716 | 0.83 | 0.93 | 0.991 | 1.32 | 1.056
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 145 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 7 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 4.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | WILO | Turbin | 16 | 20
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PD-550MA |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification