## Datasheet(PD-G050M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-G050M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 50 |  | 3000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.1 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 1 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 5 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 198.5 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP
14 | Speed |  | 3450 | rpm | Rated Power | 0.08 | kW | Shaft |  | SM20C+STS316L or STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | PP
17 |  | Suction | - | - | □FF □RF | - |  | Hose Coupling |  | pp
18 |  | Discharge | Φ20,25,11/4" | - | □FF □RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Impeller |  | SPS
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Seal Cover |  | SPS
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | ■Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 80W |  | Input | 170 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | ED-560-012 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 55 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 4.5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 4.5 |  | kg
REMARKS

## Datasheet(PD-G050MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PD-G050M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 50 |  | 3000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.1 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 1 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 5 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 198.5 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | PP
14 | Speed |  | 3450 | rpm | Rated Power | 0.08 | kW | Shaft |  | SM20C+STS316L or STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Body |  | PP
17 |  | Suction | - | - | □FF □RF | - |  | Hose Coupling |  | pp
18 |  | Discharge | Φ20,25,11/4" | - | □FF □RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Impeller |  | SPS
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Seal Cover |  | SPS
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | ■Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 80W |  | Input | 170 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | BERGMANN | Model & Size | ED-560-012 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 55 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 4.5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 4.5 |  | kg
REMARKS

## Outline Drawing(PD-G050M)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 50(Ht=1m) |  | MOTOR | OUTPUT |  |  |  | W | 80
| TOTAL HEAD | m | 5.5 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm |  | - |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | SEMI OPEN
| MAKER | WILO Pumps |  |  |  | MAKER |  |  |  | WILO Pumps
[7 empty] | TYPE |  | DARINAGE PUMP
[7 empty] | MODEL |  | PD-G050M
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PD TYPE
Φ15, Φ20, Φ25
HOSE COUPLING
1”
PIPE
Φ155
34.5
198.5

## Outline Drawing(PD-G050MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 50(Ht=1m) |  | MOTOR | OUTPUT |  |  |  | W | 80
| TOTAL HEAD | m | 5.5 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm |  | - |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID | WATER |  |  |  | TYPE |  |  |  | SEMI OPEN
| MAKER | WILO Pumps |  |  |  | MAKER |  |  |  | WILO Pumps
[7 empty] | TYPE |  | DARINAGE PUMP
[7 empty] | MODEL |  | PD-G050MA
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PD TYPE
Φ15, Φ20, Φ25
HOSE COUPLING
1”
PIPE
Φ155
34.5
198.5

## Sectional Drawing(PD-G050M)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS | AISI | DIN | (EA)
1 | CABLE ASS'Y | 2PNCT | - | - | 1 | 10 | SEAL COVER |  |  | SPS | - | - | 1
2 | HANDLE | PP | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+Cera | - | - | 1
3 | CAPACITOR | - | - | - | 1 | 12 | OIL SEAL |  |  | NBR607 | - | - | 1
4 | BODY | PP | - | - | 1 | 13 | IMPELLER |  |  | PBT | - | - | 1
5 | MOTOR ASS'Y | - | - | - | 1 | 14 | STRAINER |  |  | ABS | - | - | 1
6 | BOLTS | STS304 | 304 | X5CrNi189 | 6 | 15 | CASING |  |  | PP | - | - | 1
7 | O-RING | NBR607 | - | - | 1 | 16 | O-RING |  |  | NBR607 | - | - | 1
8 | COVER PLATE | STS304 | 304 | X5CrNi189 | 1 | 17 | GASKET |  |  | NBR607 | - | - | 1
9 | OIL SEAL | NBR607 | - | - | 1 | 18 | HOSE COUPLING |  |  | PP | - | - | 1
[8 empty] | TYPE |  | DARINAGE PUMP
[8 empty] | MODEL |  | PD-G050M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PD TYPE
1
2
3
4
5
15
7
8
9
10
11
12
13
6
14
16
17
18

## Sectional Drawing(PD-G050MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS | AISI | DIN | (EA)
1 | CABLE ASS'Y | 2PNCT | - | - | 1 | 10 | SEAL COVER |  |  | SPS | - | - | 1
2 | HANDLE | PP | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+Cera | - | - | 1
3 | CAPACITOR | - | - | - | 1 | 12 | OIL SEAL |  |  | NBR607 | - | - | 1
4 | BODY | PP | - | - | 1 | 13 | IMPELLER |  |  | PBT | - | - | 1
5 | MOTOR ASS'Y | - | - | - | 1 | 14 | STRAINER |  |  | ABS | - | - | 1
6 | BOLTS | STS304 | 304 | X5CrNi189 | 6 | 15 | CASING |  |  | PP | - | - | 1
7 | O-RING | NBR607 | - | - | 1 | 16 | O-RING |  |  | NBR607 | - | - | 1
8 | COVER PLATE | STS304 | 304 | X5CrNi189 | 1 | 17 | GASKET |  |  | NBR607 | - | - | 1
9 | OIL SEAL | NBR607 | - | - | 1 | 18 | HOSE COUPLING |  |  | PP | - | - | 1
[8 empty] | TYPE |  | DARINAGE PUMP
[8 empty] | MODEL |  | PD-G050MA
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PD TYPE
1
2
3
4
5
15
7
8
9
10
11
12
13
6
14
16
17
18

## Test Report(PD-G050M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 19 | 35 | 45 | 55 | 67 | 82
Dis. Head | (m) | 7.2 | 6 | 5 | 4 | 3 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021233 | 0.07205 | 0.1191 | 0.17792 | 0.26403 | 0.39548
Total Head | (m) | 7.2 | 6.0212 | 5.0721 | 4.1191 | 3.1779 | 2.264 | 1.3955
Water Power | (㎾) | 0 | 0.018648 | 0.028936 | 0.030214 | 0.02849 | 0.024725 | 0.018652
Shaft Power | (㎾) | 0.104 | 0.1144 | 0.1248 | 0.1304 | 0.1336 | 0.136 | 0.1368
Pump Eff. | (%) | 0 | 16.3005 | 23.1859 | 23.17 | 21.3249 | 18.1805 | 13.6345
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.6 | 0.66 | 0.72 | 0.74 | 0.76 | 0.78 | 0.78
Motor Input | (㎾) | 0.13 | 0.143 | 0.156 | 0.163 | 0.167 | 0.17 | 0.171
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.8 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 1 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 1.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | WILO | Turbin | 27 | 22
Item No. | N.A |  | Serial No. | 80700004 | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PD-G050M |  | Customer |  |  |  | 1 |  | 08.07.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PD-G050MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 16 | 28 | 43 | 53 | 64 | 80
Dis. Head | (m) | 7 | 6 | 5 | 4 | 3 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.015057 | 0.046112 | 0.10875 | 0.16522 | 0.24091 | 0.37643
Total Head | (m) | 7 | 6.0151 | 5.0461 | 4.1088 | 3.1652 | 2.2409 | 1.3764
Water Power | (㎾) | 0 | 0.015687 | 0.02303 | 0.028798 | 0.027344 | 0.023377 | 0.017949
Shaft Power | (㎾) | 0.1032 | 0.1128 | 0.1216 | 0.1304 | 0.1344 | 0.1368 | 0.1376
Pump Eff. | (%) | 0 | 13.9072 | 18.9395 | 22.0845 | 20.3455 | 17.0886 | 13.044
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.59 | 0.65 | 0.69 | 0.74 | 0.77 | 0.78 | 0.78
Motor Input | (㎾) | 0.129 | 0.141 | 0.152 | 0.163 | 0.168 | 0.171 | 0.172
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.8 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 1 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 1.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | WILO | Turbin | 27 | 22
Item No. | N.A |  | Serial No. | 80700013 | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PD-G050MA |  | Customer |  |  |  | 1 |  | 08.07.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification