## Datasheet(PDN-1400M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-1400M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 16 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 335 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IRC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1350 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 175 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 30 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 30 |  | kg
REMARKS

## Datasheet(PDN-1400MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-1400MA |  |  | Title | Submersible Pump for Sump with Automation
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 16 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 335 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IRC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1350 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 175 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 31 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 31 |  | kg
REMARKS

## Datasheet(PDN-1403M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-1403M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 16 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 335 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | BrC3
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IRC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1350 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 175 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 30 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 30 |  | kg
REMARKS

## Datasheet(PDN-1400M with AD-50)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-1400M + AD-50 |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 16 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 335 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IRC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | ■Yes □No |  | Adapter Model | AD-50
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1350 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 175 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 30 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 10 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 40 |  | kg
REMARKS

## Datasheet(PDN-1400MA with AD-50
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-1400MA + AD-50 |  |  | Title | Submersible Pump for Sump with Automation
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 16 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 335 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IRC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | ■Yes □No |  | Adapter Model | AD-50
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1350 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 175 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 31 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 10 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 41 |  | kg
REMARKS

## Datasheet(PDN-1403M with AD-50)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDN-1403M + AD-50 |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.7 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 7 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 16 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 335 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | BrC3
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IRC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1350 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 175 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 30 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 10 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 40 |  | kg
REMARKS

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 300(Ht=7m) |  | MOTOR | OUTPUT |  |  |  | W | 950
|  | TOTAL HEAD | m | 16 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (NON CLOG ,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDN-1400M/MA, -1403M
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDN TYPE

## Outline Drawing(withAD-50)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 250 |  | MOTOR | OUTPUT |  |  |  | W | 950
|  | TOTAL HEAD | m | 6 |  |  | VOLTAGE |  |  |  | V | 380
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDN-1400M/MA,1403M + AD-50
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV TYPE with ADAPTER

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | SCP1 | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+SiC |  | - | - | 1
2 | CABLE ASS'Y | 2PNCT | - | - | 1 | 12 | O-RING |  |  | NBR710 |  | - | - | 1
3 | HEAD COVER | GC150 | Class No 25 | GG15 | 1 | 13 | OIL CASING |  |  | GC150 |  | Class No 25 | GG15 | 1
4 | GASKET | NBR607 | - | - | 1 | 14 | OIL SEAL |  |  | NBR709 |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | FLANGE |  |  | NBR707 |  | - | - | 1
6 | SWITCH ASS'Y | - | - | - | 1 | 16 | SLEEVE |  |  | STS316 |  | - | - | 1
7 | O.L.P | - | - | - | 1 | 17 | IMPELLER(PDN-1400M) |  |  | GC200 |  | Class No 30 | GG20 | 1
8 | ROTOR ASS'Y | - | - | - | 1 |  | IMPELLER(PDN-1403M) |  |  | BrC3 |  | - | - | 1
9 | FRAME ASS'Y | - | - | - | 1 | 18 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
10 | MOTOR ASS'Y | - | - | - | 1 | 19 | FLANGE |  |  | GCD450 |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(NON CLOG,NON AUTO)
[8 empty] | MODEL |  | PDN-1400M/MA, -1403M
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDN TYPE

## Sectional Drawing(with AD-50 )
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI |  | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | SCP1 | - |  | - | 1 | 14 | OIL SEAL |  |  | NBR709 |  | - | - | 1
2 | CABLE ASS'Y | 2PNCT | - |  | - | 1 | 15 | FLANGE |  |  | NBR707 |  | - | - | 1
3 | HEAD COVER | GC150 | Class No 25 |  | GG15 | 1 | 16 | SLEEVE |  |  | STS316 |  | - | - | 1
4 | GASKET | NBR607 | - |  | - | 1 | 17 | IMPELLER(PDN-1400M) |  |  | GC200 |  | Class No 30 | GG20 | 1
5 | CAPACITOR | - | - |  | - | 1 |  | IMPELLER(PDN-1403M) |  |  | BrC3 |  | - | - | 1
6 | SWITCH ASS'Y | - | - |  | - | 1 | 18 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
7 | O.L.P | - | - |  | - | 1 | 19 | GUIDE HOLDER |  |  | SS400 |  | - | - | 1
8 | ROTOR ASS'Y | - | - |  | - | 1 | 20 | SLIDE |  |  | GC200 |  | - | - | 1
9 | FRAME ASS'Y | - | - |  | - | 1 | 21 | GUIDE RING |  |  | STS304 |  | - | - | 2
10 | MOTOR ASS'Y | - | - |  | - | 1 | 22 | FLANGE |  |  | GCD450 |  | - | - | 1
11 | MECHANICAL SEAL | SiC+SiC | - |  | - | 1 | 23 | CONNECTOR |  |  | GC200 |  | - | - | 1
12 | O-RING | NBR710 | - |  | - | 1 | 24 | FLOAT SWITCH |  |  | - |  | - | - | 1
13 | OIL CASING | GC150 | Class No 25 |  | GG15 | 1 | 25
[9 empty] | TYPE |  | DRAINAGE PUMP
|  |  |  | ``` | [6 empty] | (NON CLOG,NON AUTO)
[9 empty] | MODEL |  | PDN-1400M/MA, -1403M + AD-50
SERVICE
[9 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING of
PDN TYPE with ADTAPTER

## Test Report(PDN-1400(3)M_MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 55 | 120 | 178 | 226 | 326 | 372 | 402
Dis. Head | (m) | 19.2 | 17 | 15 | 13 | 11 | 7 | 5 | 3.7
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01112 | 0.052935 | 0.11647 | 0.18776 | 0.39067 | 0.5087 | 0.59406
Total Head | (m) | 19.2 | 17.0111 | 15.0529 | 13.1165 | 11.1878 | 7.3907 | 5.5087 | 4.2941
Water Power | (㎾) | 0 | 0.1525 | 0.29444 | 0.38056 | 0.41213 | 0.39273 | 0.33403 | 0.28137
Shaft Power | (㎾) | 0.721 | 0.7875 | 0.8652 | 0.917 | 0.9345 | 0.9562 | 0.9478 | 0.9352
Pump Eff. | (%) | 0 | 19.3657 | 34.0309 | 41.5007 | 44.1021 | 41.0715 | 35.2422 | 30.0869
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.3 | 6.67 | 7.12 | 7.43 | 7.55 | 7.67 | 7.67 | 7.57
Motor Input | (㎾) | 1.03 | 1.125 | 1.236 | 1.31 | 1.335 | 1.366 | 1.354 | 1.336
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 7 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 8.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Turbin | 32 | 21
Item No. | N.A |  | Serial No. |  | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PDN-1400M/MA,1403M |  | Customer |  |  |  | 1 |  | 08.07.28
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification