## Datasheet(PDV-270MLA)
SUBMERSIBLE PUMP DATA SHEET
| Model | PDV-270MLA |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 145 |  | 8700
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.3 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 3 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 9 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 266 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3300 | rpm | Rated Power | 0.3 | kW | Shaft |  | SM20C+STS316 or STS316
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150 or 200
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC200
18 |  | Discharge | Φ32, 1¼" | - | □FF □RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Oil Case |  | GC150
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3300 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.3 |  | Input | 400 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-012 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 140 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 14.5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 15 |  | kg
REMARKS

## Outline Drawing(PDV-270MLA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 145(Ht=3m) |  | MOTOR | OUTPUT |  |  |  | W | 300
|  | TOTAL HEAD | m | 9 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 40 (32) |  | No. OF REVOLUTION |  |  |  | r.p.m | 3300
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-270MLA
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PD TYPE

## Sectional Drawing(PDV-270MLA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | ABS | - | - | 1 | 10 | MECHANICAL SEAL |  |  | Cera+Sic |  | - | - | 1
2 | CABLE ASS'Y | 2PNCT | - | - | 1 | 11 | SEAL OIL |  |  | NBR709 |  | - | - | 1
3 | HEAD COVER | GC200 | Class No 30 | GG20 | 1 | 12 | O-RING |  |  | NBR |  | - | - | 1
4 | GASKET COVER | NBR | - | - | 1 | 13 | OIL CASE |  |  | GC150 |  | Class No 25 | GG15
5 | CAPACITOR | 14㎌ | - | - | 1 | 14 | O-RING |  |  | NBR |  | - | - | 1
6 | ROTOR ASS'Y | - | - | - | 1 | 15 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
7 | FRAME ASS'Y | - | - | - | 1 | 16 | IMPELLER |  |  | GC200 |  | Class No 30 | GG20 | 1
8 | MOTOR ASS'Y | - | - | - | 1 | 17 | Hose Coupling |  |  | PP |  | - | - | 1
9 | OIL SEAL | NBR709 | - | - | 1 | 18 | Float S/W | [6 empty] | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,NON AUTO)
[8 empty] | MODEL |  | PDV-270MLA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PD TYPE

## Test Report(PDV-270MLA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 48 | 89 | 127 | 147 | 160 | 177 | 192
Dis. Head | (m) | 9.4 | 8 | 7 | 5 | 4 | 3 | 2 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.050483 | 0.17356 | 0.3534 | 0.47347 | 0.56092 | 0.68645 | 0.80772
Total Head | (m) | 9.4 | 8.0505 | 7.1736 | 5.3534 | 4.4735 | 3.5609 | 2.6864 | 1.8077
Water Power | (㎾) | 0 | 0.062987 | 0.10407 | 0.11082 | 0.10719 | 0.092869 | 0.077507 | 0.056574
Shaft Power | (㎾) | 0.16146 | 0.19665 | 0.22701 | 0.2484 | 0.25323 | 0.2553 | 0.25668 | 0.25668
Pump Eff. | (%) | 0 | 32.03 | 45.8424 | 44.6138 | 42.3287 | 36.3763 | 30.1958 | 22.0409
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.13 | 1.35 | 1.55 | 1.66 | 1.69 | 1.7 | 1.72 | 1.72
Motor Input | (㎾) | 0.234 | 0.285 | 0.329 | 0.36 | 0.367 | 0.37 | 0.372 | 0.372
Motor Eff. | (%) | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 145 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.3 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 3 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 2.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 69 | Maker | WILO | Turbin | 32 | 22
Item No. | N.A |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PDV-270MLA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification