## Datasheet(PDV-400MLA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-400MLA |  |  | Title | Submersible Pump for Sump with Automation
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 130 |  | 7800
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 8 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 303 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.4 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO PUMPS Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.4 |  | Input | 660 |  | Impeller |  |  | Set(s)
33 | Protector |  | ■ Over Load Protector(O.L.P) □Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 255 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO PUMPS Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 20 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 20 |  | kg
REMARKS

## Outline Drawing(PDV-400MLA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 130(Ht=6m) |  | MOTOR | OUTPUT |  |  |  | KW | 400
|  | TOTAL HEAD | m | 8 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX, AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-400MLA
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV TYPE

## Sectional Drawing(PDV-400MLA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | ABS | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+SiC |  | - | - | 1
2 | CABLE ASS'Y | 2PNCT | - | - | 1 | 12 | O-RING |  |  | NBR710 |  | - | - | 1
3 | HEAD COVER | GC150 | Class No 25 | GG15 | 1 | 13 | OIL CASING |  |  | GC150 |  | Class No 25 | GG15 | 1
4 | GASKET | NBR607 |  |  | 1 | 14 | OIL SEAL |  |  | NBR709 |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | GASKET |  |  | NBR707 |  | - | - | 1
6 | SWITCH ASS'Y | - | - | - | 1 | 16 | SLEEVE |  |  | STS316 |  | - | - | 1
7 | O.L.P | - | - | - | 1 | 17 | IMPELLER |  |  | GC200 |  | Class No 30 | GG20 | 1
8 | ROTOR ASS'Y | - | - | - | 1 | 18 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
9 | FRAME ASS'Y | - | - | - | 1 | 19 | FLANGE |  |  | GC200 |  | - | - | 1
10 | MOTOR ASS'Y | - | - | - | 1 | 20 | LEVEL SWITCH |  |  | - |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,AUTO)
[8 empty] | MODEL |  | PDV-400MLA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV TYPE

## Test Report(PDV-400MLA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 84 | 142 | 170 | 225 | 249 | 258
Dis. Head | (m) | 9.1 | 8 | 7 | 6 | 5 | 3 | 2 | 1.6
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.025938 | 0.074123 | 0.10624 | 0.1861 | 0.22792 | 0.24469
Total Head | (m) | 9.1 | 8.0092 | 7.0259 | 6.0741 | 5.1062 | 3.1861 | 2.2279 | 1.8447
Water Power | (㎾) | 0 | 0.065275 | 0.096199 | 0.14059 | 0.14149 | 0.11685 | 0.090424 | 0.077577
Shaft Power | (㎾) | 0.2784 | 0.32665 | 0.3599 | 0.40294 | 0.42706 | 0.44988 | 0.45966 | 0.46944
Pump Eff. | (%) | 0 | 19.983 | 26.7291 | 34.8918 | 33.1321 | 25.9736 | 19.672 | 16.5254
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.32 | 3.49 | 3.6 | 3.9 | 4.02 | 4.12 | 4.18 | 4.21
Motor Input | (㎾) | 0.427 | 0.501 | 0.552 | 0.618 | 0.655 | 0.69 | 0.705 | 0.72
Motor Eff. | (%) | 65.2 | 65.2 | 65.2 | 65.2 | 65.2 | 65.2 | 65.2 | 65.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 4.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 65.2 | Maker | WILO | Turbin | 27 | 22
Item No. | N.A |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PDV-400MLA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification