## Datasheet(PDV-750M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-750M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 250 |  | 15000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 11 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 295 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Three Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1250 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 255 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 24 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 24 |  | kg
REMARKS

## Datasheet(PDV-750M+AD-50)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-750M + AD-50 |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 250 |  | 15000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 11 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 295 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | ■Yes □No |  | Adapter Model | AD-50
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Three Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1250 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 255 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 24 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 10 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 34 |  | kg
REMARKS

## Datasheet(PDV-750MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-750MA |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 250 |  | 15000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 11 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 295 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1250 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 255 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 24 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 24 |  | kg
REMARKS

## Datasheet(PDV-750MA+AD-50)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-750MA + AD-50 |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 250 |  | 15000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 11 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 295 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | GC200
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS410 or STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | GC200
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | GC150
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | GC150
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Connector |  | GC200
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Sleeve |  | STS316
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | ■Yes □No |  | Flange |  | GC200
22 | Adapter |  | ■Yes □No |  | Adapter Model | AD-50
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6203ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1250 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 255 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 24 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 10 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 34 |  | kg
REMARKS

## Outline Drawing(PDV-750M)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 250 |  | MOTOR | OUTPUT |  |  |  | W | 950
|  | TOTAL HEAD | m | 6 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VOLUTE,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-750M
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV TYPE

## Outline Drawing(with AD-50)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 250 |  | MOTOR | OUTPUT |  |  |  | W | 950
|  | TOTAL HEAD | m | 6 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO Pumps Ltd. |  |  |  | MAKER |  |  |  | WILO Pumps Ltd.
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-750M
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV TYPE with ADAPTER

## Sectional Drawing(PDV-750M)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | ABS | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+SiC |  | - | - | 1
2 | CABLE ASS'Y | 2PNCT | - | - | 1 | 12 | O-RING |  |  | NBR710 |  | - | - | 1
3 | HEAD COVER | GC150 | Class No 25 | GG15 | 1 | 13 | OIL CASING |  |  | GC150 |  | Class No 25 | GG15 | 1
4 | GASKET | NBR607 | - | - | 1 | 14 | OIL SEAL |  |  | NBR709 |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | GASKET |  |  | NBR707 |  | - | - | 1
6 | SWITCH ASS'Y | - | - | - | 1 | 16 | SLEEVE |  |  | STS316 |  | - | - | 1
7 | O.L.P | - | - | - | 1 | 17 | IMPELLER |  |  | GC200 |  | Class No 30 | GG20 | 1
8 | ROTOR ASS'Y | - | - | - | 1 | 18 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
9 | FRAME ASS'Y | - | - | - | 1 | 19 | FLANGE |  |  | GC200 |  | - | - | 1
10 | MOTOR ASS'Y | - | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,NON AUTO)
[8 empty] | MODEL |  | PDV-750M
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV TYPE

## Sectional Drawing (PDV-750MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HANDLE | ABS | - | - | 1 | 11 | MECHANICAL SEAL |  |  | SiC+SiC |  | - | - | 1
2 | CABLE ASS'Y | 2PNCT | - | - | 1 | 12 | O-RING |  |  | NBR710 |  | - | - | 1
3 | HEAD COVER | GC150 | Class No 25 | GG15 | 1 | 13 | OIL CASING |  |  | GC150 |  | Class No 25 | GG15 | 1
4 | GASKET | NBR607 | - | - | 1 | 14 | OIL SEAL |  |  | NBR709 |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | GASKET |  |  | NBR707 |  | - | - | 1
6 | SWITCH ASS'Y | - | - | - | 1 | 16 | SLEEVE |  |  | STS316 |  | - | - | 1
7 | O.L.P | - | - | - | 1 | 17 | IMPELLER |  |  | GC200 |  | Class No 30 | GG20 | 1
8 | ROTOR ASS'Y | - | - | - | 1 | 18 | CASING |  |  | GC200 |  | Class No 30 | GG20 | 1
9 | FRAME ASS'Y | - | - | - | 1 | 19 | FLANGE |  |  | GC200 |  | - | - | 1
10 | MOTOR ASS'Y | - | - | - | 1 | 20 | FlLOAT SWITCH |  |  | - |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,NON AUTO)
[8 empty] | MODEL |  | PDV-750MA
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV TYPE

## Sectional Drawing(with AD50)
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | DRAINAGE PUMP
(VORTEX,NON AUTO)
MODEL |  | PDV-750M + AD-50
SERVICE
SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV TYPE with ADAPTER
2PNCT
GC200

## Test Report(PDV-750M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 68 | 180 | 213 | 266 | 309 | 327 | 339
Dis. Head | (m) | 13.8 | 11 | 9 | 8 | 6 | 4 | 3 | 2.6
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.016998 | 0.1191 | 0.16678 | 0.2601 | 0.35099 | 0.39307 | 0.42245
Total Head | (m) | 13.8 | 11.017 | 9.1191 | 8.1668 | 6.2601 | 4.351 | 3.3931 | 3.0225
Water Power | (㎾) | 0 | 0.12211 | 0.26755 | 0.28354 | 0.27143 | 0.21915 | 0.18085 | 0.16701
Shaft Power | (㎾) | 0.4529 | 0.567 | 0.7399 | 0.7924 | 0.882 | 0.931 | 0.9555 | 0.9653
Pump Eff. | (%) | 0 | 21.5366 | 36.1609 | 35.7827 | 30.7739 | 23.5388 | 18.9277 | 17.3015
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.04 | 5.52 | 6.47 | 6.77 | 7.27 | 7.59 | 7.75 | 7.8
Motor Input | (㎾) | 0.647 | 0.81 | 1.057 | 1.132 | 1.26 | 1.33 | 1.365 | 1.379
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 250 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 8.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Turbin | 28 | 22
Item No. | N.A |  | Serial No. |  | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PVD-750M |  | Customer |  |  |  | 1 |  | 08.07.30
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PDV-750MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 68 | 180 | 213 | 266 | 309 | 327 | 339
Dis. Head | (m) | 13.8 | 11 | 9 | 8 | 6 | 4 | 3 | 2.6
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.016998 | 0.1191 | 0.16678 | 0.2601 | 0.35099 | 0.39307 | 0.42245
Total Head | (m) | 13.8 | 11.017 | 9.1191 | 8.1668 | 6.2601 | 4.351 | 3.3931 | 3.0225
Water Power | (㎾) | 0 | 0.12211 | 0.26755 | 0.28354 | 0.27143 | 0.21915 | 0.18085 | 0.16701
Shaft Power | (㎾) | 0.4529 | 0.567 | 0.7399 | 0.7924 | 0.882 | 0.931 | 0.9555 | 0.9653
Pump Eff. | (%) | 0 | 21.5366 | 36.1609 | 35.7827 | 30.7739 | 23.5388 | 18.9277 | 17.3015
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.04 | 5.52 | 6.47 | 6.77 | 7.27 | 7.59 | 7.75 | 7.8
Motor Input | (㎾) | 0.647 | 0.81 | 1.057 | 1.132 | 1.26 | 1.33 | 1.365 | 1.379
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 250 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 8.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Turbin | 28 | 22
Item No. | N.A |  | Serial No. |  | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PDV-750MA |  | Customer |  |  |  | 1 |  | 08.07.30
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification