## Datasheet(PDV-A400M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-A400M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 170 |  | 10200
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 10 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 293 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | BRASS
14 | Speed |  | 3450 | rpm | Rated Power | 0.6 | kW | Shaft |  | SM20C+STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | STS304
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | PP
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Flange |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Cover,Casing |  | PP
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Bolts |  | STS304
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6302ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO PUMPS Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.6 |  | Input | 780 |  | Impeller |  |  | Set(s)
33 | Protector |  | □Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 410 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO PUMPS Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 12 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | - |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 12 |  | kg
REMARKS

## Datasheet(PDV-A400MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-A400MA |  |  | Title | Submersible Pump for Sump with Automation
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 170 |  | 10200
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 10 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 293 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | BRASS
14 | Speed |  | 3450 | rpm | Rated Power | 0.6 | kW | Shaft |  | SM20C+STS410
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | STS304
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | PP
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Flange |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | □Yes ■No |  | Cover,Casing |  | PP
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Bolts |  | STS304
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | ■Stand □Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6302ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO PUMPS Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.6 |  | Input | 780 |  | Impeller |  |  | Set(s)
33 | Protector |  | □Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Sleeve |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 410 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO PUMPS Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 13 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter |  |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 13 |  | kg
REMARKS

## Outline Drawing(PDV-A400M)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 170(Ht=6m) |  | MOTOR | OUTPUT |  |  |  | KW | 0.6
|  | TOTAL HEAD | m | 10 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-A400M
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV-A TYPE

## Outline Drawing(PDV-A400MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 170(Ht=6m) |  | MOTOR | OUTPUT |  |  |  | KW | 0.6
|  | TOTAL HEAD | m | 10 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX,AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-A400MA
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV-A TYPE

## Sectional Drawing(PDV-A400M)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HEAD COVER | PP | - | - | 1 | 11 | GASKET |  |  | NBR610 |  | - | - | 1
2 | CABLE ASS'Y | - | - | - | 1 | 12 | FLANGE |  |  | PBT |  | - | - | 1
3 | GASKET | NBR610 | - | - | 1 | 13 | GASKET |  |  | NR607 |  | - | - | 1
4 | HOLDER CABLE | PP | - | - | 1 | 14 | CASING COVER |  |  | PP |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | CASING |  |  | PP |  | - | - | 1
6 | ROTOR ASS'Y | - | - | - | 1 | 16 | CONICAL WASHER |  |  | STS304 |  | 304 | X5CrNi189 | 1
7 | FRAME ASS'Y | STS304 | 304 | X5CrNi189 | 1 | 17 | IMPELLER |  |  | Brass |  | - | - | 1
8 | END BRACKET(B) | Aℓ | - | - | 1 | 18 | GASKET |  |  | NBR710 |  | - | - | 1
9 | END BRACKET(A) | Aℓ | - | - | 1 | * | BOLTS,NUTS |  |  | STS304 |  | 304 | X5CrNi189 | -
10 | MECHANICAL SEAL | SiC+SiC | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,NON AUTO)
[8 empty] | MODEL |  | PDV-A400M
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV-A TYPE

## Sectional Drawing(PDV-A400MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HEAD COVER | PP | - | - | 1 | 11 | GASKET |  |  | NBR610 |  | - | - | 1
2 | CABLE ASS'Y | - | - | - | 1 | 12 | FLANGE |  |  | PBT |  | - | - | 1
3 | GASKET | NBR610 | - | - | 1 | 13 | GASKET |  |  | NR607 |  | - | - | 1
4 | HOLDER CABLE | PP | - | - | 1 | 14 | CASING COVER |  |  | PP |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | CASING |  |  | PP |  | - | - | 1
6 | ROTOR ASS'Y | - | - | - | 1 | 16 | CONICAL WASHER |  |  | STS304 |  | 304 | X5CrNi189 | 1
7 | FRAME ASS'Y | STS304 | 304 | X5CrNi189 | 1 | 17 | IMPELLER |  |  | Brass |  | - | - | 1
8 | END BRACKET(B) | Aℓ | - | - | 1 | 18 | GASKET |  |  | NBR710 |  | - | - | 1
9 | END BRACKET(A) | Aℓ | - | - | 1 | * | BOLTS,NUTS |  |  | STS304 |  | 304 | X5CrNi189 | -
10 | MECHANICAL SEAL | SiC+SiC | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,AUTO)
[8 empty] | MODEL |  | PDV-A400MA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV-A TYPE

## Test Report(PDV-A400M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 42 | 125 | 203 | 227 | 248 | 272 | 290
Dis. Head | (m) | 11.6 | 10 | 8 | 6 | 5 | 4 | 3 | 2.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0064845 | 0.057438 | 0.15149 | 0.18942 | 0.22609 | 0.27197 | 0.30915
Total Head | (m) | 11.6 | 10.0065 | 8.0574 | 6.1515 | 5.1894 | 4.2261 | 3.272 | 2.6092
Water Power | (㎾) | 0 | 0.068504 | 0.16417 | 0.20355 | 0.19201 | 0.17084 | 0.14507 | 0.12333
Shaft Power | (㎾) | 0.44548 | 0.4736 | 0.53502 | 0.59422 | 0.59274 | 0.58756 | 0.58608 | 0.58534
Pump Eff. | (%) | 0 | 14.4646 | 30.6849 | 34.2544 | 32.3943 | 29.0754 | 24.7519 | 21.0706
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.02 | 3.303 | 3.77 | 4.137 | 4.117 | 4.112 | 4.073 | 4.1
Motor Input | (㎾) | 0.602 | 0.64 | 0.723 | 0.803 | 0.801 | 0.794 | 0.792 | 0.791
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 170 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.6 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | WILO | Turbin | 32 | 29
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PDV-A400M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PDV-A400MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 45 | 119 | 200 | 220 | 241 | 262 | 294
Dis. Head | (m) | 11.5 | 10 | 8 | 6 | 5 | 4 | 3 | 1.6
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.007444 | 0.052056 | 0.14704 | 0.17792 | 0.21351 | 0.25234 | 0.31774
Total Head | (m) | 11.5 | 10.0074 | 8.0521 | 6.147 | 5.1779 | 4.2135 | 3.2523 | 1.9177
Water Power | (㎾) | 0 | 0.073405 | 0.15619 | 0.20039 | 0.18568 | 0.16552 | 0.13889 | 0.091902
Shaft Power | (㎾) | 0.44548 | 0.481 | 0.53872 | 0.59792 | 0.60236 | 0.5957 | 0.59422 | 0.59422
Pump Eff. | (%) | 0 | 15.2608 | 28.992 | 33.5151 | 30.8255 | 27.7857 | 23.3742 | 15.466
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.28 | 3.007 | 3.3 | 3.632 | 3.663 | 3.665 | 3.606 | 3.628
Motor Input | (㎾) | 0.602 | 0.65 | 0.728 | 0.808 | 0.814 | 0.805 | 0.803 | 0.803
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 170 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.6 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | WILO | Turbin | 22 | 25
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PDV-A400MA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification