## Datasheet(PDV-A750M)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-A750M |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 15 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 310 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | BRASS
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS316L or STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | STS304
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | PP
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Flange |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Cover,Casing |  | PP
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Bolts |  | STS304
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | □Stand ■Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6302ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO PUMPS Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1500 |  | Impeller |  |  | Set(s)
33 | Protector |  | □Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Head Cover |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 410 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Casing Cover |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 15 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | - |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 15 |  | kg
REMARKS

## Datasheet(PDV-A750MA)
| SUBMERSIBLE PUMP DATA SHEET | [10 empty] | ■ Protector
| Model | PDV-A750MA |  |  | Title | Submersible Pump for Sump with Automation
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 300 |  | 18000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.6 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 6 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 15 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 310 | mm | (Part's Name) |  | (Symbol)
| Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Impeller |  | BRASS
14 | Speed |  | 3450 | rpm | Rated Power | 0.95 | kW | Shaft |  | SM20C+STS316L or STS316L
15 | Rotation Viewde From Driver |  |  | ■Clockwisew □Counterclockwise |  |  |  | Casing |  | PP
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Frame |  | STS304
17 |  | Suction | - | - | □FF □RF | - |  | Head Cover |  | PP
18 |  | Discharge | Φ50 | - | □FF ■RF | □Top ■Side |  | Cable |  | IEC57(2PNCT)
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Flange |  | PBT
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Cover,Casing |  | PP
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Bolts |  | STS304
22 | Adapter |  | □Yes ■No |  | Adapter Model
23 | Discharge Type |  | □Hose Connection ■Flange Conection
24 | Struction of Inlet |  | □Stand ■Strainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling ■Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6202ZZ |  | Lower : 6302ZZ |  |  | Frame | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO PUMPS Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 0.95 |  | Input | 1500 |  | Impeller |  |  | Set(s)
33 | Protector |  | □Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Shaft |  |  | Set(s)
34 | SEAL PART | [6 empty] | Head Cover |  |  | Set(s)
35 | Mechanical Seal |  | Maker | NEK | Model & Size | ED-560-015 |  | Bearing |  |  | Set(s)
36 |  |  | Type | Double Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 410 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO PUMPS Ltd.) | [6 empty] | Casing Cover |  |  | Set(s)
39 | ■ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 15 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | - |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 15 |  | kg
REMARKS

## Outline Drawing(PDV-A750M)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 300(Ht=6m) |  | MOTOR | OUTPUT |  |  |  | KW | 950
|  | TOTAL HEAD | m | 15 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX,NON AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-A750M
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV-A TYPE

## Outline Drawing(PDV-A750MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
| PUMP | CAPACITY | ℓ/min | 300(Ht=6m) |  | MOTOR | OUTPUT |  |  |  | KW | 950
|  | TOTAL HEAD | m | 15 |  |  | VOLTAGE |  |  |  | V | 220
|  | SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
|  | DISCHARGE BORE | mm | Ø | 50 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
|  | LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
|  | MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[8 empty] | TYPE |  | DRAINAGE PUMP
C.W.L : Continuous Running | [9 empty] | (VORTEX,AUTO)
|  | Water Level | [5 empty] | MODEL |  | PDV-A750MA
L.W.L : Least Running | [7 empty] | SERVICE
Water Level
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PDV-A TYPE

## Sectional Drawing(PDV-A750M)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HEAD COVER | PP | - | - | 1 | 11 | GASKET |  |  | NBR610 |  | - | - | 1
2 | CABLE ASS'Y | - | - | - | 1 | 12 | FLANGE |  |  | PBT |  | - | - | 1
3 | GASKET | NBR610 | - | - | 1 | 13 | GASKET |  |  | NR607 |  | - | - | 1
4 | HOLDER CABLE | PP | - | - | 1 | 14 | CASING COVER |  |  | PP |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | CASING |  |  | PP |  | - | - | 1
6 | ROTOR ASS'Y | - | - | - | 1 | 16 | CONICAL WASHER |  |  | STS304 |  | 304 | X5CrNi189 | 1
7 | FRAME ASS'Y | STS304 | 304 | X5CrNi189 | 1 | 17 | IMPELLER |  |  | Brass |  | - | - | 1
8 | END BRACKET(B) | Aℓ | - | - | 1 | 18 | GASKET |  |  | NBR710 |  | - | - | 1
9 | END BRACKET(A) | Aℓ | - | - | 1 | * | BOLTS,NUTS |  |  | STS304 |  | 304 | X5CrNi189 | -
10 | MECHANICAL SEAL | SiC+SiC | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,NON AUTO)
[8 empty] | MODEL |  | PDV-A750M
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV-A TYPE

## Sectional Drawing(PDV-A750MA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | HEAD COVER | PP | - | - | 1 | 11 | GASKET |  |  | NBR610 |  | - | - | 1
2 | CABLE ASS'Y | - | - | - | 1 | 12 | FLANGE |  |  | PBT |  | - | - | 1
3 | GASKET | NBR610 | - | - | 1 | 13 | GASKET |  |  | NR607 |  | - | - | 1
4 | HOLDER CABLE | PP | - | - | 1 | 14 | CASING COVER |  |  | PP |  | - | - | 1
5 | CAPACITOR | - | - | - | 1 | 15 | CASING |  |  | PP |  | - | - | 1
6 | ROTOR ASS'Y | - | - | - | 1 | 16 | CONICAL WASHER |  |  | STS304 |  | 304 | X5CrNi189 | 1
7 | FRAME ASS'Y | STS304 | 304 | X5CrNi189 | 1 | 17 | IMPELLER |  |  | Brass |  | - | - | 1
8 | END BRACKET(B) | Aℓ | - | - | 1 | 18 | GASKET |  |  | NBR710 |  | - | - | 1
9 | END BRACKET(A) | Aℓ | - | - | 1 | * | BOLTS,NUTS |  |  | STS304 |  | 304 | X5CrNi189 | -
10 | MECHANICAL SEAL | SiC+SiC | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VORTEX,AUTO)
[8 empty] | MODEL |  | PDV-A750MA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PDV-A TYPE

## Prformance Curve(PDV-A750M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 46 | 114 | 190 | 247 | 313 | 349 | 366
Dis. Head | (m) | 17.2 | 15 | 13 | 11 | 9 | 6 | 4 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0077785 | 0.047774 | 0.1327 | 0.22427 | 0.36014 | 0.44774 | 0.49243
Total Head | (m) | 17.2 | 15.0078 | 13.0478 | 11.1327 | 9.2243 | 6.3601 | 4.4477 | 3.4924
Water Power | (㎾) | 0 | 0.11253 | 0.24245 | 0.34478 | 0.37138 | 0.32449 | 0.25302 | 0.20835
Shaft Power | (㎾) | 0.67795 | 0.73755 | 0.82695 | 0.9387 | 0.9983 | 1.043 | 1.0654 | 1.0654
Pump Eff. | (%) | 0 | 15.257 | 29.319 | 36.7295 | 37.2011 | 31.111 | 23.7498 | 19.5571
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 4.1 | 4.5 | 5.04 | 5.72 | 6.1 | 6.38 | 6.5 | 6.52
Motor Input | (㎾) | 0.91 | 0.99 | 1.11 | 1.26 | 1.34 | 1.4 | 1.43 | 1.43
Motor Eff. | (%) | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 7.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74.5 | Maker | WILO | Turbin | 27 | 23
Item No. | N.A |  | Serial No. |  | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PDV-A751M |  | Customer |  |  |  | 1 |  | 08.07.24
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Prformance Curve(PDV-A750MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 47 | 120 | 203 | 256 | 315 | 354 | 364
Dis. Head | (m) | 17.2 | 15 | 13 | 11 | 9 | 6 | 4 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0081204 | 0.052935 | 0.15149 | 0.24091 | 0.36475 | 0.46067 | 0.48706
Total Head | (m) | 17.2 | 15.0081 | 13.0529 | 11.1515 | 9.2409 | 6.3648 | 4.4607 | 3.4871
Water Power | (㎾) | 0 | 0.11498 | 0.25532 | 0.36899 | 0.3856 | 0.3268 | 0.25739 | 0.20689
Shaft Power | (㎾) | 0.6705 | 0.73755 | 0.84185 | 0.96105 | 1.0132 | 1.0505 | 1.0654 | 1.0579
Pump Eff. | (%) | 0 | 15.5891 | 30.3279 | 38.3946 | 38.0581 | 31.1103 | 24.1601 | 19.5571
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 4.01 | 4.45 | 5.07 | 5.81 | 6.15 | 6.4 | 6.5 | 6.44
Motor Input | (㎾) | 0.9 | 0.99 | 1.13 | 1.29 | 1.36 | 1.41 | 1.43 | 1.42
Motor Eff. | (%) | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 6 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 7.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74.5 | Maker | WILO | Turbin | 27 | 23
Item No. | N.A |  | Serial No. |  | Inspector | J.S.JANG | Run (Hr) | B/R (℃) | Test Date
Model | PDV-A750MA |  | Customer |  |  |  | 1 |  | 08.07.24
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification