## Datasheet(TS40_13LA)
SUBMERSIBLE PUMP DATA SHEET
| Model | TS40/13LA |  |  | Title | Submersible Pump for Sump
1 | Customer |  |  |  |  | Agent No.
2 | Location |  |  |  |  | Date Issued
3 | Item No. |  |  |  |  | Plant Name
4 | Service |  |  |  |  | Quantity | Set(s)
5 | OPERATING CONDITION
6 | Liquid Pumped |  | Drainage Water |  |  | Capacity |  | 150 |  | 9000
7 | Pumping Temp. |  | Winter : -5 ℃ |  |  | Disch.Press | 0.5 |  |  |  | kgf/㎠G
8 |  |  | Summer : +40 ℃ |  |  | Total Head | 5 |  |  |  | m
9 | Specific Gravity at Pumping Temp. |  |  | 1 kgf/㎠A |  | Total Head at zero point |  |  | 13 |  | m
10 | Viscosity at Pumping Temp. |  |  | 5 Cp |  | Liquid pH |  |  | 6.5~9 |  | pH
11 | PERFORMANCE AND CONSTRUCTIONS | [6 empty] | MATERIALS
12 | Axis Position |  | □Horizontal ■Vertical |  | C.W.L | 54 | mm | (Part's Name) |  | (Symbol)
13 | Number of Stages |  | 1 Stage |  | Eff. Expected |  | % | Handle |  | STS304
14 | Speed |  | 3450 | rpm | Rated Power | 0.6 | kW | Pump Housing |  | STS304
15 | Rotation Viewde From Driver |  |  | ■Clockwise □Counterclockwise |  |  |  | Motor Housing |  | STS304
16 | Bore |  | Size(Dia) | Rating | Facing | Position |  | Impeller |  | STS304
17 |  | Suction | - | - | □FF □RF | - |  | Seal Cover |  | mPPO
18 |  | Discharge | Φ40,11/2" | - | □FF □RF | ■Top □Side |  | Casing |  | SPS
19 | Impeller Type |  | □Close ■Semi-Open □Open |  |  | Single Suction |  | Strainer |  | STS304
20 | Flow Direction |  | ■Radial □Mixed □Axial |  | Oil Seal | ■Yes □No |  | Cable Holder |  | STS304
21 | Shaft Seal |  | ■Mech. Seal □Gland |  | Shaft Sleeve | □Yes ■No |  | Hose Coupling |  | pp
22 | Adapter |  | □Yes ■No |  | Adapter Model |  |  | Cable |  | IEC57(2PNCT)
23 | Discharge Type |  | ■Hose Connection □Flange Conection
24 | Struction of Inlet |  | □Stand ■Srtainer |  |  |  |  | HYDROSTATIC
25 | Struction of Outlet |  | □Elbow ■Hose Coupling □Flange Coupling □Connector |  |  |  |  | Casing | kgf/㎠ |  | min.
26 | Bearings |  | Upper : 6201ZZ |  | Lower : 6201ZZ |  |  | Seal Cover | kgf/㎠ |  | min.
27 | PUMP DRIVER | [6 empty] | TESTING
28 | ■ Motor □ Engine □ Turbine |  |  | Maker | WILO Pumps Ltd. |  |  | (Items) |  |  | (Witness)
29 | Type |  | Single Phase Induction Motor(Submersible Type) |  |  |  |  | Run Perform. | ■Yes □No |  | □Yes ■No
30 | Starting Method |  | Line |  | Power Supply | 1Phase 220V 60Hz |  | Hydrostatic | ■Yes □No |  | □Yes ■No
31 | Pole & Speed |  | 2 | 3450 | Insulation Class | B |  | SPARE PARTS
32 | Absorbed Power |  | 600W | 0.8 | Input | 980 |  | Impeller |  |  | Set(s)
33 | Protector |  | □ Over Load Protector(O.L.P) ■Thermal Protector(T.P) |  |  |  |  | Rotor Assy |  |  | Set(s)
34 | SEAL PART | [6 empty] | Pump Housing |  |  | Set(s)
35 | Mechanical Seal |  | Maker | Burmann | Model & Size | BT-AR-012 |  | Impeller |  |  | Set(s)
36 |  |  | Type | Single Seal | Cooler Type | T-#32 |  | Casing |  |  | Set(s)
37 |  |  | Cooler | ■Yes □No | Cooler Quantity | 50 |  | M/Seal |  |  | Set(s)
38 | ACCESSORIES (Supplied by : WILO Pumps Ltd.) | [6 empty] | Name Plate |  |  | Set(s)
39 | □ Companion Flange
40 | □ Chain
41 | □ Foundation Bolts & Nuts
42 | □ Guide Pipe | [6 empty] | WEIGHT
43 | □ Special Tools | [6 empty] | Pump | 8.5 |  | kg
44 | □ Spare Parts | [6 empty] | Adapter | 0 |  | kg
45 | ■ Hose Coupling | [6 empty] | Total Wt. | 8.5 |  | kg
REMARKS

## Outline Drawing(TS40_13LA)
Sheet No.
CUSTOMER
ITEM No.
DATE
CAPACITY | ℓ/min | 150(Ht=5m) |  | MOTOR | OUTPUT |  |  |  | W | 600
TOTAL HEAD | m | 13 |  |  | VOLTAGE |  |  |  | V | 220
SUCTION BORE | mm | - |  |  | FREQUENCY |  |  |  | Hz | 60
DISCHARGE BORE | mm | Ø | 40 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
LIQUID | WATER |  |  |  | TYPE |  |  |  | SEMI OPEN
MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE, AUTO)
[6 empty] | MODEL |  | TS40/13LA
SERVICE
[6 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of TS TYPE

## Sectional Drawing(TS40_13LA)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  | Q'ty | NO. | PARTS NAME |  |  | MATERIALS |  |  |  | Q'ty
|  | KS | AISI | DIN | (EA) |  |  |  |  | KS |  | AISI | DIN | (EA)
1 | CABLE ASS'Y | Rubber | - | - | 1 | 10 | O-RING |  |  | NBR607 |  | - | - | 1
2 | CABLE GASKET | NBR | - | - | 1 | 11 | HOUSING GASKET |  |  | NBR607 |  | - | - | 1
3 | PUMP HOUSING | STS304 | 304 | X5CrNi189 | 1 | 12 | SEAL COVER |  |  | SPS |  | - | - | 1
4 | MOTOR ASSY | - | - | - | 1 | 13 | O-RING |  |  | NBR607 |  | - | - | 1
5 | MOTOR HOUSING | STS304 | 304 | X5CrNi189 | 1 | 14 | OIL SEAL |  |  | NBR709 |  | - | - | 1
6 | OIL SEAL | NBR709 | - | - | 1 | 15 | IMPELLER |  |  | STS304 |  | 304 | X5CrNi189 | 1
7 | SHAFT | STS316L | 316 | - | 1 | 16 | CASING |  |  | SPS |  | - | - | 1
8 | STOP RING | STS304 | 304 | X5CrNi189 | 1 | 17 | STRAINER |  |  | STS304 |  | 304 | X5CrNi189 | 1
9 | MECHANICAL SEAL | Aℓ2O3+Sic | - | - | 1 | 18 | HOSE COUPLING |  |  | PP |  | - | - | 1
[8 empty] | TYPE |  | DRAINAGE PUMP
(VOLUTE,NON AUTO)
[8 empty] | MODEL |  | TS40/13LA
SERVICE
[8 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of TS TYPE

## Test Report(TS40_13LA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 43 | 105 | 142 | 162 | 183 | 222 | 248
Dis. Head | (m) | 13.7 | 12 | 9 | 7 | 6 | 5 | 3 | 1.6
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.016594 | 0.098946 | 0.18097 | 0.23553 | 0.30055 | 0.44231 | 0.55198
Total Head | (m) | 13.7 | 12.0166 | 9.0989 | 7.181 | 6.2355 | 5.3006 | 3.4423 | 2.152
Water Power | (㎾) | 0 | 0.084224 | 0.15573 | 0.16621 | 0.16466 | 0.15811 | 0.12456 | 0.086992
Shaft Power | (㎾) | 0.4032 | 0.4795 | 0.5362 | 0.5831 | 0.6216 | 0.6601 | 0.707 | 0.7329
Pump Eff. | (%) | 0 | 17.565 | 29.043 | 28.5047 | 26.489 | 23.9525 | 17.6186 | 11.8695
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.6 | 3.09 | 3.43 | 3.73 | 4.08 | 4.22 | 4.55 | 4.67
Motor Input | (㎾) | 0.576 | 0.685 | 0.766 | 0.833 | 0.888 | 0.943 | 1.01 | 1.047
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.60 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | WILO | Turbin | 20 | 14
Item No. |  |  | Serial No. |  | Inspector | S.K.S | Run (Hr) | B/R (℃) | Test Date
Model | TS40/13LA |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288
Suc. Head | m | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Suc. Head | m | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Vacuum | mmhg | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288 | 294.288
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification