## Datasheet
PUMP DATA SHEET
| Model | PH-080M | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity | Set(S) | ■ Indoor □ Outdoor
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 75 | ℓ/min(at Ht 4m) | NPSHav | mAq
7 | Pumping Temp | 80 ℃ | Suct.Press |  | Kg/㎠G | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press |  | Kg/㎠G | Solid
9 | Vap. Press @P.T | 1 Kg/㎠A | Diffr.Press |  | Kg/㎠G | Corros.or Erros
10 | Visc @P.T | 1 Cp | Total Head | 6 | m
11 | [5 empty] | MATERIALS
12 | ■Horizontal □Vertical |  | Efficiency |  | % | (Parts" Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 80 | W | CASING | GC150
14 | Speed | 3500 rpm | Input | 170 | W | SHAFT | STS410
15 | Rotation | ■CW □CCW | (view from driver) |  |  | IMPELLER | NORYL
16 | Bore | Size(Dia) | Rating | Face | Position
17 | Suction | 40㎜(1-1/2") | ㎏/㎠ | ■FF,□RF | □End □Top ■Side
18 | Discharge | 40㎜(1-1/2") | ㎏/㎠ | ■FF,□RF | □End □Top ■Side
19 | Impeller Type | ■Peripheral | ■Single Suct. □Double Suct |  | HYDROSTSTIC
20 | Flow Direction | ■Radial □Mixed □Axial |  |  | Casing | 3 ㎏/㎠ | 3 Min.
21 | Shaft Seal | □G/P, ■M/S | Shaft Sleeve | □Yes ■No | Jacket | ㎏/㎠ | Min.
22 | Mounting | □Foot □Centerline □Bracket |  |  | TESTING
23 | Lubrication Type | □Grease □Oil Bath |  |  | (Items) |  | (witness)
24 | Cooling | □Stuff.Box □B/R Housing ■No Cooling |  |  | Run Perform. | ■Yes □No | □Yes ■No
25 | Radial Bearings | #608zz | Thrust Bearing | #608zz | Hydrostatic | ■Yes □No | □Yes ■No
26 | PUMP DRIVER |  |  |  |  | SPARE PARTS
27 | ■Motor □Engine □Turbine |  | V/Phase/Hz | 220 / 1Φ / 60 |  |  | Set(S)
28 | Maker | WILO | Motor Frame No. |  |  |  | Set(S)
29 | Type | SEMI OPEN | Furnished by | ■ WILO □ Customer |  |  | Set(S)
30 | Power | 80W | Mounted | ■ WILO □ Customer |  |  | Set(S)
31 | Pole & Speed | 2p 3500rpm | Insulation Class | ■ B □E □ F |  |  | Set(S)
32 | ACCESSORIES (□Supplied : WILO) | [5 empty] | Set(S)
33 | □Base Plate | □ Steel Channel |  |  |  |  | Set(S)
34 | □Foundation Bolts & Nuts | [5 empty] | Set(S)
35 | Coupling | □ Sun Flex □ Flange □ Grid |  |  | □Coupling Guard |  | Set(S)
36 | □Press. Gauge | [5 empty] | Set(S)
37 | □Collar or Plug for Drain & Air Vent. | [5 empty] | Set(S)
38 | □Sealing Flushing Pipe | [5 empty] | Set(S)
39 | ■Mechanical | Maker | NEK | Model & Size | PAI 8
40 | Seal | Type |  | Cooler | NO
41 |  | API 610 Plan |  |  |  | WEIGHT
42 | ■ Companion Flange |  |  |  |  | Pump / Bed | ㎏
43 | □ Special Tools |  |  |  |  | Driver | ㎏
44 | [5 empty] | Total Wt. | 6.5 ㎏

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | HOT WATER CIRCULATION
MODEL |  | PH-080M
SERVICE
SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PH TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS | [5 empty] | Q'ty(ea)
|  | KS | ASTM | DIN
1 | CASING | GC150 | CLASS NO.30 | - |  |  |  | 1
2 | IMPELLER | NORYL | - | - |  |  |  | 1
3 | MECHANICAL SEAL | CERAMIC+CARBON | - | - |  |  |  | 1
4 | O-RING | NBR | - | - |  |  |  | 1
5 | NUT | SM20C | - | - |  |  |  | 4
6 | GASKET | NBR | - | - |  |  |  | 2
7 | FLANGE | GC200 | CLASS NO.35 | - |  |  |  | 2
8 | BOLT | SM20C | - | - |  |  |  | 4
9 | CAPACITOR COVER | P.P | - | - |  |  |  | 1
10 | MOTOR | - | - | - |  |  |  | 1
11 | BEARING CAP | NBR | - | - |  |  |  | 1
|  |  |  | TYPE |  | HOT WATER CIRCULATION
|  |  |  | MODEL |  | PH-080M
SERVICE
|  |  |  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PH TYPE

## TEST REPORT
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 33 | 66 | 80 | 92 | 104 | 117 | 120
Dis. Head | (m) | 8.2 | 7 | 5 | 4 | 3 | 2 | 1 | 0.65
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 8.2 | 7 | 5 | 4 | 3 | 2 | 1 | 0.65
Water Power | (㎾) | 0 | 0.037653 | 0.05379 | 0.05216 | 0.044988 | 0.033904 | 0.019071 | 0.012714
Shaft Power | (㎾) | 0.064114 | 0.083142 | 0.084816 | 0.087048 | 0.087606 | 0.087048 | 0.085932 | 0.085932
Pump Eff. | (%) | 0 | 45.2876 | 63.4196 | 59.921 | 51.3526 | 38.9486 | 22.1931 | 14.7954
Speed | (rpm) | 3444 | 3348 | 3337 | 3330 | 3327 | 3327 | 3334 | 3334
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.52 | 0.672 | 0.687 | 0.7 | 0.703 | 0.7 | 0.69 | 0.69
Motor Input | (㎾) | 0.1149 | 0.149 | 0.152 | 0.156 | 0.157 | 0.156 | 0.154 | 0.154
Motor Eff. | (%) | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 75 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.08 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 4 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 40
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 55.8 | Maker | O.S | Turbin | 15 | 15
Item No. |  |  | Serial No. |  | Inspector | S.G.S | Run (Hr) | B/R (℃) | Test Date
Model | PH-080M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification