## Datesheet
PUMP DATA SHEET
| Model | PH-600I | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity | Set(S) | ■ Indoor □ Outdoor
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 13 | ℓ/min(at Ht 11m)
7 | Pumping Temp | 80 ℃ | Suct.Press |  | Kg/㎠G
8 | Sp. Gr. @P.T | 1 | Disch.Press |  | Kg/㎠G
9 | Vap. Press @P.T | 1 Kg/㎠A | Diffr.Press |  | Kg/㎠G
10 | Visc @P.T | 1 Cp | Total Head | 11 | m
11 | [5 empty] | MATERIALS
12 | ■Horizontal □Vertical |  | Efficiency |  | % | (Parts" Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 600 | W | CASING | GC150
14 | Speed | 3500 rpm | Input | 620 | W | SHAFT | STS410
15 | Rotation | ■CW □CCW | (view from driver) |  |  | IMPELLER | mPPO(Noryl)
16 | Bore | Size(Dia) | Rating | Face | Position
17 | Suction | 65mm(2-1/2") | Kg/㎠ | ■FF,□RF | □End □Top ■Side
18 | Discharge | 65mm(2-1/2") | Kg/㎠ | ■FF,□RF | □End □Top ■Side
19 | Impeller Type | ■Peripheral | ■Single Suct. □Double Suct |  | HYDROSTSTIC
20 | Flow Direction | ■Radial □Mixed □Axial |  |  | Casing | 4 Kg/㎠ | 3 Min.
21 | Shaft Seal | □G/P, ■M/S | Shaft Sleeve | □Yes ■No | Jacket | Kg/㎠ | Min.
22 | Mounting | ■Foot □Centerline □Bracket |  |  | TESTING
23 | Lubrication Type | □Grease □Oil Bath |  |  | (Items) |  | (witness)
24 | Cooling | □Stuff.Box □B/R Housing ■No Cooling |  |  | Run Perform. | ■Yes □No | □Yes ■No
25 | Radial Bearings | #6202zz | Thrust Bearing | #6202zz | Hydrostatic | ■Yes □No | □Yes ■No
26 | PUMP DRIVER |  |  |  |  | SPARE PARTS
27 | ■Motor □Engine □Turbine |  | V/Phase/Hz | 220/380 / 3Φ / 60 |  |  | Set(S)
28 | Maker | WILO | Motor Frame No. |  |  |  | Set(S)
29 | Type | CLOSED | Furnished by | ■ WILO □ Customer |  |  | Set(S)
30 | Power | 600W | Mounted | ■ WILO □ Customer |  |  | Set(S)
31 | Pole & Speed | 2p 3500rpm | Insulation Class | ■B □ E □ F |  |  | Set(S)
32 | ACCESSORIES (□Supplied : WILO) | [5 empty] | Set(S)
33 | □Base Plate | □ Steel Channel |  |  |  |  | Set(S)
34 | □Foundation Bolts & Nuts | [5 empty] | Set(S)
35 | Coupling | □ Sun Flex □ Flange □ Grid |  |  | □Coupling Guard |  | Set(S)
36 | □Press. Gauge | [5 empty] | Set(S)
37 | □Collar or Plug for Drain & Air Vent. | [5 empty] | Set(S)
38 | □Sealing Flushing Pipe | [5 empty] | Set(S)
39 | ■Mechanical | Maker | NEK | Model & Size | PAI 15
40 | Seal | Type |  | Cooler | NO
41 |  | API 610 Plan |  |  |  | WEIGHT
42 | ■ Companion Flange |  |  |  |  | Pump / Bed | Kg
43 | □ Special Tools |  |  |  |  | Driver | Kg
44 | [5 empty] | Total Wt. | 20 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 85(Ht=10m) |  | MOTOR | OUTPUT |  |  |  | W | 600
| TOTAL HEAD | m | 11 |  |  | VOLTAGE |  |  |  | V | 220/380
| SUCTION BORE | mm | Ø | 65 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 65 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3500
| LIQUID | WATER |  |  |  | TYPE |  |  |  | CLOSED
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | HOT WATER CIRCULATION
[7 empty] | MODEL |  | PH-600I
SERVICE
[7 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PH TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS | [5 empty] | Q'ty(ea)
|  | KS | ASTM | DIN
1 | CASING | GC150 | CLASS NO.25 | GG15 |  |  |  | 1
2 | IMPELLER | Brc | - | - |  |  |  | 1
3 | MECHANICAL SEAL | CERAMIC+CARBON | - | - |  |  |  | 1
4 | O-RING | NBR | - | - |  |  |  | 1
5 | NUT | SM20C | - | - |  |  |  | 8
6 | GASKET | NBR | - | - |  |  |  | 2
7 | FLANGE | GC200 | CLASS NO.30 | GG20 |  |  |  | 2
8 | BOLT | SM20C | - | - |  |  |  | 8
9 | TERMINAL COVER | P.P | - | - |  |  |  | 1
10 | MOTOR | - | - | - |  |  |  | 1
11 | FAN | PBT | [5 empty] | 1
12 | FAN COVER | ABS | - | - |  |  |  | 1
|  |  |  | TYPE |  | HOT WATER CIRCULATION
|  |  |  | MODEL |  | PH-600I
SERVICE
|  |  |  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PH TYPE

## TestReport(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 89.5 | 182 | 215 | 239 | 294 | 317 | 343
Dis. Head | (m) | 11.4 | 10 | 8 | 7 | 6 | 4 | 3 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 11.4 | 10 | 8 | 7 | 6 | 4 | 3 | 2
Water Power | (㎾) | 0 | 0.14588 | 0.23733 | 0.24532 | 0.23374 | 0.19169 | 0.15501 | 0.11182
Shaft Power | (㎾) | 0.32529 | 0.40834 | 0.44602 | 0.45525 | 0.44756 | 0.42526 | 0.41141 | 0.39604
Pump Eff. | (%) | 0 | 35.7264 | 53.2102 | 53.886 | 52.2261 | 45.0758 | 37.678 | 28.2344
Speed | (rpm) | 3516 | 3489 | 3477 | 3471 | 3471 | 3477 | 3482 | 3484
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 2.27 | 2.4 | 2.47 | 2.49 | 2.47 | 2.41 | 2.4 | 2.37
Motor Input | (㎾) | 0.423 | 0.531 | 0.58 | 0.592 | 0.582 | 0.553 | 0.535 | 0.515
Motor Eff. | (%) | 76.9 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 290 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 4 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 65 | 65
Efficiency |  | (%) | Volt. (V) | 220/380 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76.9 | Maker | WILO | Turbin | 11 | 19
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PH-600I |  | Customer |  |  |  | 1 |  | 2012.11.28
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 94 | 130 | 215.5 | 264 | 293 | 316.5 | 347
Dis. Head | (m) | 11.4 | 10 | 9 | 7 | 5 | 4 | 3 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 11.4 | 10 | 9 | 7 | 5 | 4 | 3 | 2
Water Power | (㎾) | 0 | 0.15322 | 0.19071 | 0.24589 | 0.21516 | 0.19104 | 0.15477 | 0.11312
Shaft Power | (㎾) | 0.31914 | 0.41603 | 0.43141 | 0.45679 | 0.44294 | 0.43218 | 0.41141 | 0.3945
Pump Eff. | (%) | 0 | 36.8292 | 44.2063 | 53.8295 | 48.575 | 44.2031 | 37.6186 | 28.675
Speed | (rpm) | 3521 | 3492 | 3486 | 3476 | 3477 | 3477 | 3483 | 3490
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.3 | 1.39 | 1.41 | 1.43 | 1.4 | 1.4 | 1.36 | 1.37
Motor Input | (㎾) | 0.415 | 0.541 | 0.561 | 0.594 | 0.576 | 0.562 | 0.535 | 0.513
Motor Eff. | (%) | 76.9 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 290 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 4 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 65 | 65
Efficiency |  | (%) | Volt. (V) | 220/380 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76.9 | Maker | WILO | Turbin | 11 | 19
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PH-600I |  | Customer |  |  |  | 1 |  | 2012.11.28
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification