## Datasheet
PUMP DATA SHEET
| Model | PH-950U | Title |  |  | Sheet No.
1 | Customer | WILO |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity | Set(S) | ■ Indoor □ Outdoor
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 260 | ℓ/min(at Ht 4m) | NPSHav | mAq
7 | Pumping Temp | 80 ℃ | Suct.Press |  | Kg/㎠G | Concentration | %
8 | Sp. Gr. @P.T | 1 | Disch.Press |  | Kg/㎠G | Solid
9 | Vap. Press @P.T | 1 Kg/㎠A | Diffr.Press |  | Kg/㎠G | Corros.or Erros
10 | Visc @P.T | 1 Cp | Total Head | 19 | m
11 | [5 empty] | MATERIALS
12 | ■Horizontal □Vertical |  | Efficiency |  | % | (Parts" Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 950 | W | CASING | GC150
14 | Speed | 3500 rpm | Input | 1360 | W | SHAFT | STS410
15 | Rotation | ■CW □CCW | (view from driver) |  |  | IMPELLER | BrC3
16 | Bore | Size(Dia) | Rating | Face | Position
17 | Suction | 50mm(2") | Kg/㎠ | ■FF,□RF | □End □Top ■Side
18 | Discharge | 50mm(2") | Kg/㎠ | ■FF,□RF | □End □Top ■Side
19 | Impeller Type | □Peripheral | ■Single Suct. □Double Suct |  | HYDROSTSTIC
20 | Flow Direction | ■Radial □Mixed □Axial |  |  | Casing | 4 Kg/㎠ | 3 Min.
21 | Sealing | □G/P, ■M/S | Shaft Sleeve | □Yes ■No | Jacket | Kg/㎠ | Min.
22 | Mounting | □Foot □Centerline □Bracket |  |  | TESTING
23 | Lubrication Type | □Grease □Oil Bath |  |  | (Items) |  | (witness)
24 | Cooling | □Stuff.Box □B/R Housing ■No Cooling |  |  | Run Perform. | ■Yes □No | □Yes ■No
25 | Radial Bearings | #6204/6202zz | Thrust Bearing |  | Hydrostatic | ■Yes □No | □Yes ■No
26 | PUMP DRIVER |  |  |  |  | SPARE PARTS
27 | ■Motor □Engine □Turbine |  | V/Phase/Hz | 380 / 3Φ / 60 |  |  | Set(S)
28 | Maker | WILO | Motor Frame No. |  |  |  | Set(S)
29 | Type | CLOSE | Furnished by | ■ WILO □ Customer |  |  | Set(S)
30 | Power | 950W | Mounted | ■ WILO □ Customer |  |  | Set(S)
31 | Pole & Speed | 2p 3500rpm | Insulation Class | □ B □ E ■ F |  |  | Set(S)
32 | ACCESSORIES (□Supplied : WILO) | [5 empty] | Set(S)
33 | □Base Plate | □ Steel Channel |  |  |  |  | Set(S)
34 | □Foundation Bolts & Nuts | [5 empty] | Set(S)
35 | Coupling | □ Sun Flex □ Flange □ Grid |  |  | □Coupling Guard |  | Set(S)
36 | □Press. Gauge | [5 empty] | Set(S)
37 | □Collar or Plug for Drain & Air Vent. | [5 empty] | Set(S)
38 | □Sealing Flushing Pipe | [5 empty] | Set(S)
39 | ■Mechanical | Maker | NEK | Model & Size | PAI 15
40 | Seal | Type |  | Cooler | NO
41 |  | API 610 Plan |  |  |  | WEIGHT
42 | ■ Companion Flange |  |  |  |  | Pump / Bed | 8 Kg
43 | □ Special Tools |  |  |  |  | Driver | 13 Kg
44 | [5 empty] | Total Wt. | 21 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | HOT WATER CIRCULATION
MODEL |  | PH-950U
SERVICE
SCALE:N/S
OUTLINE DRAWING

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(ea)
|  | KS | ASTM | DIN
1 | CASING | GC150 | CLASS NO.30 | - |  |  | 1
2 | IMPELLER | BrC3 | - | - |  |  | 1
3 | CAP NUT | STS316 | - | - |  |  | 1
4 | WASHER PLAN | STS316 | - | - |  |  | 1
5 | MECHANICAL SEAL | CERAMIC+CARBON | - | - |  |  | 1
6 | O-RING | NBR610 | - | - |  |  | 1
7 | FLANGE | GC200 | CLASS NO.35 | - |  |  | 2
8 | MOTOR | - | - | - |  |  | -
9 | FAN COVER | SPCC1 | - | - |  |  | -
10 | FAN | PBT | - | - |  |  | 1
|  |  |  | TYPE |  | HOT WATER CIRCULATION
|  |  |  | MODEL |  | PH-950U
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PH TYPE
1
2
3
4
5
8
9
10
7
6

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 92 | 142 | 184 | 233 | 265 | 283 | 297
Dis. Head | (m) | 20.7 | 18 | 15 | 12 | 9 | 6 | 4 | 1.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 20.7 | 18 | 15 | 12 | 9 | 6 | 4 | 1.4
Water Power | (㎾) | 0 | 0.26993 | 0.34719 | 0.3599 | 0.34181 | 0.25917 | 0.18452 | 0.067775
Shaft Power | (㎾) | 0.4776 | 0.6776 | 0.7568 | 0.8024 | 0.8512 | 0.8496 | 0.8392 | 0.8216
Pump Eff. | (%) | 0 | 39.8359 | 45.8761 | 44.8534 | 40.1564 | 30.5049 | 21.9871 | 8.2492
Speed | (rpm) | 3557 | 3535 | 3524 | 3517 | 3512 | 3510 | 3510 | 3515
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.57 | 3.81 | 3.93 | 4.04 | 4.11 | 4.1 | 4.08 | 4.07
Motor Input | (㎾) | 0.597 | 0.847 | 0.946 | 1.003 | 1.064 | 1.062 | 1.049 | 1.027
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.95 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 15 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 50 | 50
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | WILO | electric
Item No. |  |  |  |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PH-950U |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification