## Datasheet
PUMP DATA SHEET
| Model | PH-K043M | Title |  |  | Sheet No.
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity | Set(S) | ■ Indoor □ Outdoor
5 | OPERATING CONDITION
6 | Liquid | Water | Flow | 35 | ℓ/min(at Ht 3m)
7 | Pumping Temp | 80 ℃ | Suct.Press |  | Kg/㎠G
8 | Sp. Gr. @P.T | 1 | Disch.Press |  | Kg/㎠G
9 | Vap. Press @P.T | 1 Kg/㎠A | Diffr.Press |  | Kg/㎠G
10 | Visc @P.T | 1 Cp | Total Head | 4.5 | m
11 | [5 empty] | MATERIALS
12 | ■Horizontal □Vertical |  | Efficiency |  | % | (Parts" Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 40 | W | CASING | GC200
14 | Speed | 3500 rpm | Input | 100 | W | SHAFT | STS410
15 | Rotation | ■CW □CCW | (view from driver) |  |  | IMPELLER | NORYL
16 | Bore | Size(Dia) | Rating | Face | Position
17 | Suction | 25mm(1") | Kg/㎠ | ■FF,□RF | □End □Top ■Side
18 | Discharge | 25mm(1") | Kg/㎠ | ■FF,□RF | □End □Top ■Side
19 | Impeller Type | Centrifugal | ■Single Suct. □Double Suct |  | HYDROSTSTIC
20 | Flow Direction | ■Radial □Mixed □Axial |  |  | Casing | 2 Kg/㎠ | 3 Min.
21 | Shaft Seal | □G/P, ■M/S | Shaft Sleeve | □Yes ■No | Jacket | Kg/㎠ | Min.
22 | Mounting | □Foot □Centerline □Bracket |  |  | TESTING
23 | Lubrication Type | □Grease □Oil Bath |  |  | (Items) |  | (witness)
24 | Cooling | □Stuff.Box □B/R Housing ■No Cooling |  |  | Run Perform. | ■Yes □No | □Yes ■No
25 | Radial Bearings | #608zz | Thrust Bearing | #608zz | Hydrostatic | ■Yes □No | □Yes ■No
26 | PUMP DRIVER |  |  |  |  | SPARE PARTS
27 | ■Motor □Engine □Turbine |  | V/Phase/Hz | 220 / 1Φ / 60 |  |  | Set(S)
28 | Maker | WILO | Motor Frame No. |  |  |  | Set(S)
29 | Type | SEMI OPEN | Furnished by | ■ WILO □ Customer |  |  | Set(S)
30 | Power | 40W (0.05HP) | Mounted | ■ WILO □ Customer |  |  | Set(S)
31 | Pole & Speed | 2p 3500rpm | Insulation Class | □B ■ E □ F |  |  | Set(S)
32 | ACCESSORIES (□Supplied : WILO) | [5 empty] | Set(S)
33 | □Base Plate | □ Steel Channel |  |  |  |  | Set(S)
34 | □Foundation Bolts & Nuts | [5 empty] | Set(S)
35 | Coupling | □ Sun Flex □ Flange □ Grid |  |  | □Coupling Guard |  | Set(S)
36 | □Press. Gauge | [5 empty] | Set(S)
37 | □Collar or Plug for Drain & Air Vent. | [5 empty] | Set(S)
38 | □Sealing Flushing Pipe | [5 empty] | Set(S)
39 | ■Mechanical | Maker | NEK | Model & Size | PAI 8
40 | Seal | Type |  | Cooler | NO
41 |  | N.E.K |  |  |  | WEIGHT
42 | ■ Companion Flange |  |  |  |  | Pump / Bed | Kg
43 | □ Special Tools |  |  |  |  | Driver | Kg
44 | [5 empty] | Total Wt. | 5 Kg

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 35(Ht=3m) |  | MOTOR | OUTPUT |  |  |  | W | 40
| TOTAL HEAD | m | 4.5 |  |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø | 25 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3500
| LIQUID | WATER |  |  |  | TYPE |  |  |  | SEMI OPEN
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | HOT WATER CIRCULATION
[7 empty] | MODEL |  | PH-K043M
SERVICE
[7 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PH TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'ty(ea)
|  | KS | ASTM | DIN
1 | CASING | GC200 | CLASS NO.35 | - |  |  | 1
2 | IMPELLER | NORYL | - | - |  |  | 1
3 | MECHANICAL SEAL | CERAMIC+CARBON | - | - |  |  | 1
4 | O-RING | NBR | - | - |  |  | 1
5 | NUT | SM20C | - | - |  |  | 4
6 | GASKET | NBR | - | - |  |  | 2
7 | FLANGE | GC200 | CLASS NO.35 | - |  |  | 2
8 | BOLT | SM20C | - | - |  |  | 4
9 | MOTOR | - | - | - |  |  | 1
10 | CAPACITOR COVER | ABS(AF-305F) | - | - |  |  | 1
11 | BEARING CAP | NBR | - | - |  |  | 1
|  |  |  | TYPE |  | HOT WATER CIRCULATION
|  |  |  | MODEL |  | PH-K043M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PH TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.1 | 31.8 | 41.1 | 48.4 | 55 | 60.5
Dis. Head | (m) | 5 | 4.5 | 4 | 3.5 | 3 | 2.5 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 5 | 4.5 | 4 | 3.5 | 3 | 2.5 | 2
Water Power | (㎾) | 0 | 0.014743 | 0.020734 | 0.023448 | 0.023668 | 0.022412 | 0.019723
Shaft Power | (㎾) | 0.038019 | 0.042389 | 0.044137 | 0.045448 | 0.046322 | 0.046759 | 0.046322
Pump Eff. | (%) | 0 | 34.7811 | 46.9756 | 51.592 | 51.0936 | 47.9319 | 42.578
Speed | (rpm) | 3439 | 3398 | 3374 | 3356 | 3347 | 3344 | 3344
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.44 | 0.48 | 0.5 | 0.51 | 0.52 | 0.52 | 0.52
Motor Input | (㎾) | 0.087 | 0.097 | 0.101 | 0.104 | 0.106 | 0.107 | 0.106
Motor Eff. | (%) | 43.7 | 43.7 | 43.7 | 43.7 | 43.7 | 43.7 | 43.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.04 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 3 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 25 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 43.7 | Maker | WILO | Turbin | 11 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PH-K043M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification