## Datasheet
PUMP DATA SHEET
| Model | RS25/6 | Title |  |  | Sheet No. | 1
1 | Customer |  |  | Agent No.
2 | Location |  |  | Date Issued
3 | Item No. |  |  | Plant Name
4 | Service |  |  | Quantity |  | Location | ■In, □Out
5 | OPERATING CONDITION
6 | Liquid | Clean Water | Flow | 25 | ℓ/min (at Ht=4m)
7 | Pumping Temp | AMB. ℃ | Suct.Head | - | m
8 | Sp. Gr. @P.T | 1 | Disch.Press | 6 | m
9 | Vap. Press @P.T | Kg/㎠A | Total Head | 6 | m
10 | Visc @P.T | Cp
11 | [5 empty] | MATERIALS
12 | ■ Horizontal | □ Vertical | Efficiency | - | % | (Parts' Name) | Symbol(KS)
13 | Number of Stages | 1 Stage | Rated Power | 40 | W | Casing | GC200
14 | Speed | 3400 rpm | NPSHre | - | mAq | Shaft | STS420
15 | Rotation | □ CW, ■ CCW | Column Head | - | m | Impeller | PP
16 | Bore | Size(Dia) | Rating | Face | Position | Bearing | Carbon
17 | Suction | 25A | 10K | □ FF, □ RF | □End □Top ■Side
18 | Discharge | 25A | 10K | □ FF, □ RF | □Top, ■Side
19 | Impeller Type | Closed | ■Single Suct. | □Double Suct. | HYDROSTATIC
20 | Flow Direction | ■ Radial | □ Mixed | □ Axial | Casing | 10 Kg/㎠ | 3 Min.
21 | Shaft Seal | □ G/Packing | ■ M/Seal
22 | Shaft Sleeve | □Yes, □No
23 | Mounting | □ Foot | □ Centerline | □ Bracket | TESTING
24 | Lubrication Type | □ Grease | □ Oil Bath | ■ N.A | (Items) |  | (witness)
25 | Cooling | □ Stuff.Box | □B/R Housing | □ No. Cooling | Run Perform. | ■ Yes □ No | □Yes □No
26 | Radial Bearings | - | Thrust Bearing | - | Hydrostatic | ■ Yes □ No | □Yes □No
27 | PUMP DRIVER |  |  |  |  | SPARE PARTS
28 | Motor | V/Phase/Hz | 220 | 1 | 60 | Impeller | Set(S)
29 | Maker | WILO Pumps Ltd. |  |  |  | Shaft | Set(S)
30 | Type | INDUCTION MOTOR |  |  |  | Shaft Sleeve | Set(S)
31 | Power | 40W |  |  |  | Casing Ring | Set(S)
32 | Pole & Speed | 2 p 3400 rpm | Insulation Class | F | IP44 | Bearing(R+T) | Set(S)
33 | ACCESSORIES |  |  |  |  | Bearing(Journal) | Set(S)
34 | □Base Plate | □ Cast Iron | □Steel Plate |  | □ Drain Rim | M/Seal | Set(S)
35 | □Foundation Bolts & Nuts |  |  |  |  | Casing Gasket | Set(S)
36 | Coupling | □ Sun Flex | □ WOODS | □ Grid | □Coupling Guard | Oil Seal | Set(S)
37 | □Press. Gauge | □Suct.Vacuum □Suct.Compound □Suct.Press □Disch.Press |  |  |  | Coupling | Set(S)
38 | □Collar or Plug for Drain & Air Vent. |  |  |  |  | Coupling Rubber | Set(S)
39 | □Sealing Flushing Pipe |  | □ Cooling Piping |  |  | Name Plate | Set(S)
40 |  | Maker |  | Model & Size |  |  | Set(S)
41 | Mechanical Seal | Type |  | Cooler | □Yes, ■No | WEIGHT
42 | [5 empty] | Pump / Bed | Kg
43 | □ Companion Flange |  |  |  |  | Driver | Kg
44 | □ Special Tools |  |  |  |  | Total Wt. | 2.4 Kg

## Outline drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
Demensions(mm)
a | 33
b1 | 100
b2 | 92.5
b3 | 54
b4 | 73
l4 | 79
l0 | 130
l1 | 97
l3 | 65
G | 1 1/2"
TYPE
|  | MODEL |  | RS25/6
SERVICE
SCALE:N/S
OUTLINE DRAWING
of RS type

## Curve
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.0132 | 0.025 | 0.035 | 0.042 | 0.049 | 0.0518 |  | 0.3 | 0.33 | 0.35
Dis. Head | (m) | 6.2 | 5 | 4 | 3 | 2 | 1 | 0.8 |  | 33 | 20.3 | 11.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Total Head | (m) | 6.2 | 5 | 4 | 3 | 2 | 1 | 0.8 |  | 33 | 20.3 | 11.3
Water Power | (kW) | 0 | 0.010758 | 0.0163 | 0.017115 | 0.013692 | 0.007987 | 0.0067547 |  | 1.6137 | 1.0919 | 0.64467
Shaft Power | (kW) | 0.03944 | 0.04584 | 0.05008 | 0.05256 | 0.05456 | 0.05576 | 0.056 |  | 4.192 | 4.104 | 4.024
Pump Eff. | (%) | 0 | 23.4686 | 32.5479 | 32.5628 | 25.0953 | 14.3239 | 12.062 |  | 38.4948 | 26.6067 | 16.0205
Speed | (rpm) | 3329 | 3142 | 2904 | 2726 | 2599 | 2557 | 2555 |  | 3478 | 3478 | 3482
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 380 | 380 | 380
Current | (A) | 0.232 | 0.257 | 0.288 | 0.3 | 0.308 | 0.313 | 0.313 |  | 8.86 | 8.7 | 8.57
Motor Input | (kW) | 0.0493 | 0.0573 | 0.0626 | 0.0657 | 0.0682 | 0.0697 | 0.07 |  | 5.24 | 5.13 | 5.03
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.025 | (㎥/min) | Phase(Φ) | 1 | Output(kW) | 0.04 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 4 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 25 | 25 | 0
Efficiency | 30 | (%) | Volt.(v) | 220 | Current(A) | 0.37 | Flow Meter | R.T (℃) | W.T (℃) |  | 0
I/P Out-Dia | 25 | (mm) | Eff.(%) | 80 | M/T Maker | WILO | Turbin | 16 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | RS25/6 |  | Customer |  |  |  | 2 |  | 2009.11.02
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 125 | 130 | 140 | 155 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 1.699 | 1.767 | 1.9029 | 2.1068 | 2.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67 |  | 21.67 |  | 21.67 |  | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0 | 37.43 | 0 | 37.43 | 0 | 37.43 | 0 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification