## Datasheet
PUMP DATA SHEET
1 | Model | PM-015NM | Type | Magnet Driven Pump |  | Sheet No.
2 | Customer |  |  | Agent No.
3 | Location |  |  | Issued Date
4 | Item No. |  |  | Plant Name
5 | Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
6 | Operating Condition
7 | liquid |  | Flow | 7ℓ/min | (Ht=4m) | Min. Con. Flow | ℓ/min
8 | Pumping Temp. | 25 ℃ | Suct. Press. | - | Kgf/㎠ | Design Press. | 0.7Kgf/㎠
9 | Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 90 ℃
10 | Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
11 | Visc. @P.T | Cp | Total Head | 4.5 | m
12 | Operating Cond. | Continuous
13 | Construction & Performance |  |  |  |  | Material
14 | ■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | NORYL
15 | Number of Stages | 1 Stage | Rated Power | 15 | W | Impeller | NORYL
16 | Speed | 3450 | NPSHre | 0m |  | Shaft | Ceramics
17 | Rotation | ■ CW □ CCW | (View From Driver) |  |  | Trust Washer | Ceramics
18 | Bore | Size(Dia) | Rating | Face | Position | Bearing | CARBON
19 | Suction | 14mm HOSE | Kgf/㎠ | RF | End | Back Casing | NORYL
20 | Discharge | 14mm HOSE | Kgf/㎠ | RF | Top | O-ring | EPDM
21 | Impeller Type | open | ■ Single Suct. □ Double Suct. |  | Hydrostatic
22 | Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
23 | Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
24 | Mounting |  |  |  | Testing
25 | Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
26 | Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
27 | Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
28 | Pump Driver |  |  |  |  | Spare Parts
29 | ■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 220V/1Φ/60Hz
30 | Maker | WILO | Motor Fr. No.
31 | Type | Closed | Furnished by | ■ WILO □ Customer
32 | Power | 15w | Mounted | ■ WILO □ Customer
33 | Pole & Speed | 2p 3450rpm | Insulation Class | □ B ■ E □ F
34 | Accessories
35 | □ Base Plate
36 | □ Foundation Bolts & Nuts
37 | □ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
38 | □ Press. Gauge
39 | □ Collar or Plug for Drain & Air Vent.
40 | □ Companion Flange
41 | □ Special Tool |  |  |  |  | Weight
42 | [5 empty] | Pump/Head
43 | [5 empty] | Driver
44
45 | [5 empty] | Total Weight | 3.6 Kg
※ Don't run dry

## Outline Demesion
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 7(4m) | MOTOR | OUTPUT |  |  |  | W | 15
| TOTAL HEAD | m | 4.5 |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø14 hose |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø14 hose |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID |  |  |  | TYPE |  |  |  | closed
| MAKER | WILO |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | MAGNET PUMP
[6 empty] | MODEL |  | PM-015NM
SERVICE
[6 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING of PM TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS | [5 empty] | Q'TY
|  | KS | DIN | AISI
10 | CASING | NORYL | [5 empty] | 1
20 | IMPELLER ASSY | NORYL | [5 empty] | 1
30 | WASHER | Aℓ2O3 | [5 empty] | 2
40 | SHAFT, PUMP | Aℓ2O3 | [5 empty] | 1
50 | O-RING | EDPM | [5 empty] | 1
60 | CASING, BACK | NORYL | [5 empty] | 1
70 | MOTOR ASSY | - | [5 empty] | 1
80 | NUT | SMC440 | 42CrMo4 | 4140 |  |  |  | 1
90 | MAGNET ASSY | AℓDC+Ferrite | [5 empty] | 1
100 | SCREW, SPECIAL | STS304 | X5CrNi189 | 304 |  |  |  | 4
|  |  |  | TYPE |  | MAGNET PUMP
|  |  |  | MODEL |  | PM-015NM
SERVICE
|  |  |  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PM TYPE
10
20
30
40
50
60
70
90
80
100

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 4.4 | 8.2 | 10.9 | 12.7 | 14.4 | 14.9
Dis. Head | (m) | 5.4 | 5 | 4 | 3 | 2 | 1 | 0.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 5.4 | 5 | 4 | 3 | 2 | 1 | 0.3
Water Power | (㎾) | 0 | 0.003586 | 0.0053464 | 0.0053301 | 0.0041402 | 0.0023472 | 0.00072861
Shaft Power | (㎾) | 0.012069 | 0.012879 | 0.01381 | 0.014337 | 0.014661 | 0.015187 | 0.01543
Pump Eff. | (%) | 0 | 27.8438 | 38.7126 | 37.1772 | 28.2395 | 15.4548 | 4.7219
Speed | (rpm) | 3218 | 3134 | 3015 | 2954 | 2877 | 2815 | 2781
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.167 | 0.171 | 0.176 | 0.18 | 0.182 | 0.186 | 0.188
Motor Input | (㎾) | 0.0298 | 0.0318 | 0.0341 | 0.0354 | 0.0362 | 0.0375 | 0.0381
Motor Eff. | (%) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 7 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.015 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 4 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 14 | 14
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 40.5 | Maker | LG | Turbin | 24 | 27
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PM-015NM |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification