## Datasheet
Pump Data Sheet
Model | PM-030PM | Type | Magnet Driven Pump |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Issued Date
Item No. |  |  | Plant Name
Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
Operating Condition
liquid |  | Flow | 20ℓ/min | (Ht=2m) | Min. Con. Flow | ℓ/min
Pumping Temp. | AMB. ℃ | Suct. Press. | - | Kgf/㎠ | Design Press. | 0.7Kgf/㎠
Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 60 ℃
Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
Visc. @P.T | Cp | Total Head | 3.5 | m
Operating Cond. | Continuous
Construction & Performance |  |  |  |  | Material
■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | P.P+GF30%
Number of Stages | 1 Stage | Rated Power | 30 | W | Impeller | P.P+GF30%
Speed | 3450 | NPSHre | 0m |  | Shaft | Ceramics
Rotation | ■ CW □ CCW | (View From Driver) |  |  | Trust Washer | Ceramics
Bore | Size(Dia) | Rating | Face | Position | Bearing | PTFE
Suction | 17mm HOSE | Kgf/㎠ | RF | End | Back Casing | P.P+GF30%
Discharge | 17mm HOSE | Kgf/㎠ | RF | Top | O-ring | VITON
Impeller Type | open | ■ Single Suct. □ Double Suct. |  | Hydrostatic
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
Mounting |  |  |  | Testing
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
Pump Driver |  |  |  |  | Spare Parts
■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 220V/1Φ/60Hz
Maker | WILO | Motor Fr. No.
Type | Closed | Furnished by | ■ WILO □ Customer
Power | 30w | Mounted | ■ WILO □ Customer
Pole & Speed | 2p 3450rpm | Insulation Class | □ B ■ E □ F
Accessories
□ Base Plate
□ Foundation Bolts & Nuts
□ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
□ Press. Gauge
□ Collar or Plug for Drain & Air Vent.
□ Companion Flange
□ Special Tool |  |  |  |  | Weight
Pump/Head
Driver
[5 empty] | Total Weight | 3.6 Kg
※ Don't run dry

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 20(2m) | MOTOR | OUTPUT |  |  |  | W | 30
| TOTAL HEAD | m | 3.5 |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø17 hose |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø17 hose |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID |  |  |  | TYPE |  |  |  | closed
| MAKER | WILO |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | MAGNET PUMP
[6 empty] | MODEL |  | PM-030PM
SERVICE
[6 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PM TYPE
38
217
44
60
147
26
60
117
90
106

## Section Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS | [5 empty] | Q'TY
|  | KS | DIN | AISI
10 | CASING | PolyPropylene | [5 empty] | 1
20 | IMPELLER ASSY | PolyPropylene | [5 empty] | 1
30 | WASHER | Aℓ2O3 | [5 empty] | 2
40 | SHAFT, PUMP | Aℓ2O3 | [5 empty] | 1
50 | O-RING | VITON | [5 empty] | 1
60 | CASING, BACK | PolyPropylene | [5 empty] | 1
70 | MOTOR ASSY | - | [5 empty] | 1
80 | NUT | SMC440 | 42CrMo4 | 4140 |  |  |  | 1
90 | MAGNET ASSY | AℓDC+Ferrite | [5 empty] | 1
100 | SCREW, SPECIAL | STS304 | X5CrNi189 | 304 |  |  |  | 5
|  |  |  | TYPE |  | MAGNET PUMP
|  |  |  | MODEL |  | PM-030PM
SERVICE
|  |  |  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PM TYPE
10
20
30
40
50
60
70
90
80
100

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.4 | 15 | 18.4 | 20.8 | 23.2 | 25 | 27
Dis. Head | (m) | 4.2 | 3.5 | 3 | 2.5 | 2 | 1.5 | 1 | 0.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 4.2 | 3.5 | 3 | 2.5 | 2 | 1.5 | 1 | 0.4
Water Power | (㎾) | 0 | 0.0059332 | 0.007335 | 0.007498 | 0.0067808 | 0.0056724 | 0.004075 | 0.0017604
Shaft Power | (㎾) | 0.014144 | 0.015808 | 0.017056 | 0.017888 | 0.01872 | 0.019552 | 0.019968 | 0.0208
Pump Eff. | (%) | 0 | 37.5329 | 43.0054 | 41.9164 | 36.2222 | 29.0119 | 20.4077 | 8.4635
Speed | (rpm) | 3400 | 3343 | 3305 | 3288 | 3256 | 3221 | 3196 | 3166
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23
Motor Input | (㎾) | 0.034 | 0.038 | 0.041 | 0.043 | 0.045 | 0.047 | 0.048 | 0.05
Motor Eff. | (%) | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  | 0.17: MOTOR SPECIFICATION; 0.21: TEST CONDITION
Capacity | 20 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.02 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 2 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 17 | 17
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 41.6 | Maker | WILO | Turbin | 20 | 18
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PM-030PM | 0.17: Customer; 0.21: 2
Checked By |  | 0.19: Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification