## Datasheet
Pump Data Sheet
Model | PM-051NM | Type | Magnet Driven Pump |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Issued Date
Item No. |  |  | Plant Name
Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
Operating Condition
liquid |  | Flow | 10ℓ/min | (Ht=5m) | Min. Con. Flow | ℓ/min
Pumping Temp. | AMB | Suct. Press. | - | Kgf/㎠ | Design Press. | 1.5Kgf/㎠
Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 90 ℃
Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
Visc. @P.T | Cp | Total Head | 10 | m
Operating Cond. | Continuous
Construction & Performance |  |  |  |  | Material
■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | NORYL
Number of Stages | 1 Stage | Rated Power | 50 | W | Impeller | NORYL
Speed | 3450 | NPSHre | 0m |  | Shaft | Ceramics
Rotation | ■ CW □ CCW | (View From Driver) |  |  | Trust Washer | Ceramics
Bore | Size(Dia) | Rating | Face | Position | Bearing | CARBON
Suction | 19mm HOSE | Kgf/㎠ |  | End | Back Casing | NORYL
Discharge | 19mm HOSE | Kgf/㎠ |  | Top | O-ring | EPDM
Impeller Type | open | ■ Single Suct. □ Double Suct. |  | Hydrostatic
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
Mounting |  |  |  | Testing
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
Pump Driver |  |  |  |  | Spare Parts
■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 220V/1Φ/60Hz
Maker | WILO | Motor Fr. No.
Type | Closed | Furnished by | ■ WILO □ Customer
Power | 50w | Mounted | ■WILO □ Customer
Pole & Speed | 2p 3450rpm | Insulation Class | □ B ■ E □ F
Accessories
□ Base Plate
□ Foundation Bolts & Nuts
□ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
□ Press. Gauge
□ Collar or Plug for Drain & Air Vent.
□ Companion Flange
□ Special Tool |  |  |  |  | Weight
Pump/Head
Driver
[5 empty] | Total Weight | 5 Kg
※ Don't run dry

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 10(5m) | MOTOR | OUTPUT |  |  |  | W | 50
| TOTAL HEAD | m | 10 |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø19 hose |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø19 hose |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID |  |  |  | TYPE |  |  |  | Closed
| MAKER | WILO |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | MAGNET PUMP
[6 empty] | MODEL |  | PM-051NM
SERVICE
[6 empty] | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PM TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS | [5 empty] | Q'TY
|  | KS | DIN | AISI
10 | CASING | Noryl | [5 empty] | 1
20 | IMPELLER ASSY | Noryl | [5 empty] | 1
30 | WASHER | Aℓ2O3 | [5 empty] | 2
40 | SHAFT, PUMP | Aℓ2O3 | [5 empty] | 1
50 | O-RING | EDPM | [5 empty] | 1
60 | CASING, BACK | PolyPropylene | [5 empty] | 1
70 | MOTOR ASSY | - | [5 empty] | 1
80 | NUT | SMC440 | 42CrMo4 | 4140 |  |  |  | 1
90 | MAGNET ASSY | AℓDC+Ferrite | [5 empty] | 1
100 | SCREW, SPECIAL | STS304 | X5CrNi189 | 304 |  |  |  | 6
|  |  |  | TYPE |  | MAGNET PUMP
|  |  |  | MODEL |  | PM-051NM
SERVICE
|  |  |  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PM TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 7 | 12.2 | 15.2 | 16 | 17 | 18 | 18.6
Dis. Head | (m) | 11.6 | 10 | 8 | 6 | 5 | 4 | 2 | 0.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 11.6 | 10 | 8 | 6 | 5 | 4 | 2 | 0.2
Water Power | (㎾) | 0 | 0.01141 | 0.015909 | 0.014866 | 0.01304 | 0.011084 | 0.005868 | 0.00060636
Shaft Power | (㎾) | 0.3748 | 0.04336 | 0.04588 | 0.04812 | 0.04896 | 0.04988 | 0.05072 | 0.05108
Pump Eff. | (%) | 0 | 26.3146 | 34.6748 | 30.8928 | 26.634 | 22.2213 | 11.5694 | 1.1871
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.44 | 0.5 | 0.52 | 0.55 | 0.56 | 0.57 | 0.58 | 0.58
Motor Input | (㎾) | 0.937 | 0.1084 | 0.1147 | 0.1203 | 0.1224 | 0.1247 | 0.1268 | 0.1277
Motor Eff. | (%) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 10 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.025 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 5 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 19 | 19
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 40 | Maker | LG | Turbin | 24 | 21
Item No. |  |  | Serial No. |  | Inspector | K.I.H | Run (Hr) | B/R (℃) | Test Date
Model | PM-051NM |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification