## Datasheet
Pump Data Sheet
Model | PM-150PM | Type | Magnet Driven Pump |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Issued Date
Item No. |  |  | Plant Name
Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
Operating Condition
liquid |  | Flow | 45ℓ/min | (Ht=4m) | Min. Con. Flow | ℓ/min
Pumping Temp. | AMB | Suct. Press. | - | Kgf/㎠ | Design Press. | 1.2Kgf/㎠
Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 60 ℃
Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
Visc. @P.T | Cp | Total Head | 8 | m
Operating Cond. | Continuous
Construction & Performance |  |  |  |  | Material
■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | P.P+GF30%
Number of Stages | 1 Stage | Rated Power | 150 | W | Impeller | P.P+GF30%
Speed | 3450 | NPSHre | 0m |  | Shaft | Ceramics
Rotation | ■ CW □ CCW | (View From Driver) |  |  | Trust Washer | Ceramics
Bore | Size(Dia) | Rating | Face | Position | Bearing | PTFE
Suction | 20mm HOSE | Kgf/㎠ |  | End | Back Casing | P.P+GF30%
Discharge | 20mm HOSE | Kgf/㎠ |  | Top | O-ring | VITON
Impeller Type | OPEN | ■ Single Suct. □ Double Suct. |  | Hydrostatic
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
Mounting |  |  |  | Testing
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
Pump Driver |  |  |  |  | Spare Parts
■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 220V/1Φ/60Hz
Maker | WILO-LG | Motor Fr. No.
Type | Close | Furnished by | ■ WILO-LG □ Customer
Power | 150w | Mounted | ■ WILO-LG □ Customer
Pole & Speed | 2p 3500rpm | Insulation Class | □ B ■ E □ F
Accessories
□ Base Plate
□ Foundation Bolts & Nuts
□ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
□ Press. Gauge
□ Collar or Plug for Drain & Air Vent.
□ Companion Flange
□ Special Tool |  |  |  |  | Weight
Pump/Head
Driver
[5 empty] | Total Weight | 8.5 Kg
※ Don't run dry

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 45(4m) | MOTOR | OUTPUT |  |  |  | W | 150
| TOTAL HEAD | m | 8 |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø20 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø20 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3500
| LIQUID |  |  |  | TYPE |  |  |  | OPEN
| MAKER | WILO |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | MAGNET PUMP
[6 empty] | MODEL |  | PM-150PM
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PM TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  |  | Q'TY
|  | KS | DIN | AISI
10 | CASING | PolyPropylene |  |  |  |  | 1
20 | IMPELLER ASSY | PolyPropylene+Ferrite |  |  |  |  | 1
30 | WASHER | Aℓ2O3 |  |  |  |  | 2
40 | SHAFT, PUMP | Aℓ2O3 |  |  |  |  | 1
50 | O-RING | VITON |  |  |  |  | 1
60 | CASING, BACK | PolyPropylene |  |  |  |  | 1
70 | MOTOR ASSY | - |  |  |  |  | 1
80 | NUT | SMC440 | 42CrMo4 | 4140 |  |  | 1
90 | MAGNET ASSY | AℓDC+Ferrite |  |  |  |  | 1
100 | SCREW, SPECIAL | STS304 | X5CrNi189 | 304 |  |  | 6
|  |  |  | TYPE |  | MAGNET PUMP
|  |  |  | MODEL |  | PM-150PM
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of PM TYPE
90
70
60
50
10
20
30
40
100
80

## TestReport
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 12.1 | 29 | 38.9 | 46.4 | 52.2 | 58.6 | 73.8
Dis. Head | (m) | 8.3 | 8 | 7 | 6 | 5 | 4 | 3 | 1.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 8.3 | 8 | 7 | 6 | 5 | 4 | 3 | 1.2
Water Power | (㎾) | 0 | 0.015778 | 0.033089 | 0.038044 | 0.037816 | 0.034034 | 0.028655 | 0.014435
Shaft Power | (㎾) | 0.10658 | 0.11453 | 0.12777 | 0.13637 | 0.14365 | 0.14961 | 0.15491 | 0.16351
Pump Eff. | (%) | 0 | 13.7771 | 25.8981 | 27.8974 | 26.3244 | 22.7484 | 18.4983 | 8.8282
Speed | (rpm) | 3539 | 3530 | 3510 | 3501 | 3491 | 3481 | 3473 | 3458
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 0.94 | 0.98 | 1.05 | 1.09 | 1.14 | 1.17 | 1.2 | 1.25
Motor Input | (㎾) | 0.161 | 0.173 | 0.193 | 0.206 | 0.217 | 0.226 | 0.234 | 0.247
Motor Eff. | (%) | 66.2 | 66.2 | 66.2 | 66.2 | 66.2 | 66.2 | 66.2 | 66.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 45 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 4 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 20 | 20
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 66.2 | Maker | WILO | Turbin | 25 | 23
Item No. |  |  | Serial No. |  | Inspector | K.S.C | Run (Hr) | B/R (℃) | Test Date
Model | PM-150PM |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification