## Datasheet
PUMP DATA SHEET | [8 empty] | CUSTOMER
ITEM No.
DATE
Model |  | PM-Series |  |  | Title |  |  |  | Sheet No.
Location |  |  |  |  | Plant Name
Agent No. |  |  |  |  | Quantity
Service | [8 empty] | Location |  | ■ In, □ Out
OPERATING CONDITION
Pumping Temp. |  | Ambient |  | Design Temp. |  | 60℃ |  |  | Altitude |  | 1,000m max
Sp.Gr.@P.T |  | Below 1.05 |  | Operating Condition |  | Continuous |  |  | Kinematic viscosity |  | equivalent to water
Vap.Press.@P.T |  | kgf/㎠A |  | Humidity |  | 95% max.
Visc.@P.T |  | Below 30Cp |  | Liquid
PERFORMANCE AND CONSTRUCTIONS
|  | Model | PM-403PI PM-403PN | PM-753PI PM-753PN | PM-1503PI PM-1503PN | PM-2203PI PM-2203PN | PM-3703PI PM-3703PN | PM-403FI PM-403FN | PM-753FI PM-753FN | PM-1503FI PM-1503FN | PM-2203FI PM-2203FN | PM-3703FI PM-3703FN
Classification
Output(kW) |  |  | 0.37 | 0.75 | 1.5 | 2.2 | 3.7 | 0.37 | 0.75 | 1.5 | 2.2 | 3.7
Input(kW) |  |  | 0.53 | 0.99 | 1.6 | 2.7 | 3 | 0.53 | 0.99 | 1.6 | 2.7 | 3
Current (A) | 3 Phase | 220V | 1.5 | 2.9 | 5.39 | 7.95 | 12.6 | 1.5 | 2.9 | 5.39 | 7.95 | 12.6
|  | 380V | 0.87 | 1.68 | 3.12 | 4.6 | 7.29 | 0.87 | 1.68 | 3.12 | 4.6 | 7.29
|  | 440V | 0.75 | 1.45 | 2.69 | 3.98 | 6.3 | 0.75 | 1.45 | 2.69 | 3.98 | 6.3
Flow (l/min) | Rated Flow | Q | 100 | 180 | 230 | 300 | 300 | 100 | 180 | 230 | 300 | 300
|  | at H(m) | 8 | 12 | 20 | 20 | 25 | 8 | 12 | 20 | 20 | 25
| Max. Flow |  | 250 | 350 | 450 | 480 | 580 | 250 | 350 | 450 | 480 | 580
Shut off Head(m) |  |  | 9 | 16 | 25 | 30 | 35 | 9 | 16 | 25 | 30 | 35
Piping(mm) |  | Suct. | 40 |  | 50 |  | 50 | 40 |  | 50 |  | 50
|  | Disch. | 40 |  | 40 |  | 50 | 40 |  | 40 |  | 50
Motor (V/Phase/Hz) |  |  | I : 220/380V 3Phase 60Hz N : 440V 3Phase 60Hz
Motor Frame Size |  |  | 71 | 80 | 90L | 90L | 112M | 71 | 80 | 90L | 90L | 112M
Motor Efficiency |  |  | 76 | 77.5 | 83.5 | 84 | 86.5 | 76 | 77.5 | 83.5 | 84 | 86.5
Bearing | Pump Side |  | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ
| Fan Side |  | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ
Diameter of Impeller(mm) |  |  | 82 | 99 | 124 | 140 | 139 | 82 | 99 | 124 | 140 | 139
Impeller Type |  |  | Centrifugal Closed Impeller
Flow Direction |  |  | ■ Radial, □ Mixed, □ Axial
Weight (kg) | Pump/Head |  | 7 | 13.5 | 15 | 14.5 | 21.5 | 7.5 | 14.5 | 16 | 15.5 | 23
| Driver(Motor) |  | 13 | 17 | 25 | 28 | 47 | 13 | 17 | 25 | 28 | 47
| Net Weight |  | 20 | 30.5 | 40 | 42.5 | 68.5 | 20.5 | 31.5 | 41 | 43.5 | 70
| Gross Weight |  | 21.5 | 32.5 | 41.5 | 44.5 | 74 | 22 | 33.5 | 43 | 45.5 | 75.5
Material | Casing |  | P.P+G/F30% |  |  |  |  | PVdF
| Mouth Washer |  | Ceramic
| Impeller |  | P.P+G/F30% |  |  |  |  | PVdF
| I/P Mouth Ring |  | PTFE (Teflon)
| I/P Bearing |  | PTFE (Teflon)
| Shaft |  | Ceramic
| Rear Casing |  | P.P+G/F30% |  |  |  |  | PVdF
| O-Ring |  | Viton
| Magnet |  | Ferrite |  | NFb |  |  | Ferrite |  | NFb
| Base Plate |  | P.P+G/F30%
PUMP DRIVER
Mounting Position |  |  | ■ Hotizontal, □ Vertical |  |  | Motor Type |  | TEFC
Motor Maker |  |  | TECO (in TAIWAN) |  |  | Insulation Class |  | E
Shaft Seal |  |  | □ G/Packing, □ M/Seal, ■ None |  |  | Protecting Index |  | IP54
Pole & Speed |  |  | 2 pole / 3,450 rpm |  |  | Rotation |  | □ CW, ■ CCW (viewed from pump Head)
Motor Bearing Lubrication |  |  | ■ Grease, □ Oil Bath |  |  | Cooling |  | □ Stuff. Box, □ B/R Housing, ■ Fan cooling
TESTING | [6 empty] | HYDROSTATIC
( Items ) |  |  | ( Self test ) |  | ( Witness ) |  | Casing | 150% of Shut-Off Head |  |  |  | 3 min.
Run Performal |  |  | ■ Yes, □ No |  | □ Yes, ■ No |  | Bracket
Hydrostatic |  |  | ■ Yes, □ No |  | □ Yes, ■ No
ACCESSORIES
■ Base plate |  | □ Drain Rim |  | □ Foundation Bolts & Nuts |  |  | ■ Plug for Priming & Air Vent
Coupling |  | □ Sun Flex □ Woods □ Grid ■ No |  |  |  |  | □ Sealing Flushing Pipe □ Cooling Popin ■ No
Press. Gauge |  | □ Suct. Vacuum □ Suct. Compound □ Suct. Press □ Disch. Press ■ No
□ Companion Flange
□ Special Tools
SPARE PARTS
Impeller |  | Set(S) |  | O-Ring |  | Set(S) |  | Flange Socket |  | Set(S)
Bearing |  | Set(S) |  | Driver Magnet |  | Set(S) |  | Pump Bracket |  | Set(S)
Casing |  | Set(S) |  | Base Plate |  | Set(S) |  | Motor Assembly |  | Set(S)
Rear Casing |  | Set(S) |  | Flange |  | Set(S) |  | Set(S) |  | Set(S)
Do Not Dry Running!

## Outline Drawing
|  |  |  | OUTLINE DRAWING | [6 empty] | CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | TYPE |  |  | MAGNET DRIVEN |  |  |  | MOTOR | VOLTAGE |  |  |  |  | 220/380V or 440V
| INSTALLATION |  |  | INDOOR |  |  |  |  | FREQUENCY |  |  |  |  | 60Hz
| PIPING |  |  | FLANGE TYPE |  |  |  |  | No. of REVOLUTION |  |  |  |  | 3400 r.p.m
| LIQUID |  |  | FLUID |  |  |  |  | TYPE |  |  |  |  | TEFC
| MAKER |  |  | TRUNDEAN(TAIWAN) |  |  |  |  | MAKER |  |  |  |  | TECO (TAIWAN)
Model |  | Power |  | Output | Dimension (mm) | [9 empty] | Piping(mm) |  | Weight | Gross Weight
|  | (V) | (ph) | (W) | H | H1 | H2 | L | L 1 | L 2 | B1 | B2 | B3 | W | Suc. | Disch. | (Kg)
PM-403PI/FI |  | 220/380 | 3 | 370 | 235 | 110 | 125 | 470 | 86 | 52 | 98 | 140 | 110 | 140 | 40 | 40 | 20.0/20.5 | 24
PM-403PN/FN |  | 440 |  |  |  | 90 | 104 |  | 252 | 98.1 | 157.5 | 51 | 120 |  | 1"¼ | 1"
PM-753PI/FI |  | 220/380 | 3 | 750 | 255 | 115 | 140 | 525 | 90 | 66 | 130 | 165 | 130 | 160 |  |  | 30.5/31.5 | 35
PM-753PN/FN |  | 440
PM-1503PI/FI |  | 220/380 | 3 | 1500 | 275 | 115 | 160 | 620 | 100 | 66 | 200 | 165 | 210 | 260 | 50 | 40 | 40.0/41.0
PM-1503PN/FN |  | 440 | [15 empty] | 45
PM-2203PI/FI |  | 220/380 | 3 | 2200 | [12 empty] | 42.5/43.5 | 48
PM-2203PN/FN |  | 440
PM-3703PI/FI |  | 220/380 | 3 | 3700 | 315 | 165 | 150 | 685 | 100 | 66 | 90 | 180 | 200 | 240 | 50 | 50 | 68.5/70.0
PM-3703PN/FN |  | 440
[10 empty] | TYPE |  |  | MAGNET PUMP
[10 empty] | MODEL |  |  | PM-Series
SERVICE
[10 empty] | SCALE |  |  | N/S

## Sectional Drawing
|  | SECTIONAL DRAWING |  |  | CUSTOMER
ITEM No.
DATE
NO | PART NAME |  | MATERIAL |  |  |  | Q'TY
|  |  | PM-403PI PM-753PI | PM-1503PI | PM-403FI PM-753FI | PM-1503FI
|  |  |  | PM-2203PI |  | PM-2203FI
|  |  |  | PM-3703PI |  | PM-3703FI
1 | FLANGE SOCKET |  | PP+G/F30% |  | PVdF |  | 1
2 | O-RING |  | VITON |  |  |  | 1
3 | FLANGE |  | NYLON |  |  |  | 1
4 | BOLT |  | STS304 |  |  |  | 8
5 | FRONT CASING |  | PP+G/F30% |  | PVdF |  | 1
6 | CASING MOUTH RING |  | CERAMIC (Al2O3) |  |  |  | 1
7 | IMPELLER |  | PP+G/F30% |  | PVdF |  | 1
8 | IMPELLER MOUTH RING |  | PTFE(TEFLON) |  |  |  | 1
9 | O-RING IN CASING |  | VITON |  |  |  | 1
10 | REAR CASING |  | PP+G/F30% |  | PVdF |  | 1
11 | SHAFT |  | CERAMIC (Al2O3) |  |  |  | 1
12 | BEARING |  | PTFE(TEFLON) |  |  |  | 1
13 | MAGNET |  | FERRITE | NFb | FERRITE | NFb | 1
14 | BEARING WASHER |  | CERAMIC (Al2O3) |  |  |  | 1
15 | MAGNET HOUSING |  | GC250 |  |  |  | 1
16 | PUMP BRACKET |  | GC250 |  |  |  | 1
17 | PUMP BASE PLATE |  | PP+G/F30% |  |  |  | 1
18 | MOTOR |  | 3PHASE 220/380V or 440V 60Hz TEFC (TECO) |  |  |  | 1
[5 empty] | TYPE | MAGNET PUMP
[5 empty] | MODEL | PM-Series
SERVICE
[5 empty] | SCALE | N/S

## TestReport(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.133 | 0.234 | 0.319 | 0.427 | 0.472 | 0.505 | 0.516 | 0.524
Dis. Head | (m) | 33.9 | 32 | 28 | 24 | 16 | 12 | 8 | 4 | 2.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.093728 | 0.29013 | 0.5392 | 0.9661 | 1.1805 | 1.3513 | 1.4108
Total Head | (m) | 33.9 | 32.0937 | 28.2901 | 24.5392 | 16.9661 | 13.1805 | 9.3513 | 5.4108
Water Power | (kW) | 0 | 0.69576 | 1.079 | 1.276 | 1.1809 | 1.0141 | 0.76975 | 0.45509
Shaft Power | (kW) | 1.0819 | 1.7027 | 2.0933 | 2.2621 | 2.3478 | 2.3201 | 2.2697 | 2.1428
Pump Eff. | (%) | 0 | 40.8626 | 51.5479 | 56.4057 | 50.2963 | 43.7076 | 33.9145 | 21.2378
Speed | (rpm) | 3523 | 3467 | 3444 | 3427 | 3421 | 3419 | 3422 | 3432 | 3441
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.52 | 3.56 | 4.28 | 4.58 | 4.71 | 4.68 | 4.59 | 4.31 | 4.17
Motor Input | (kW) | 1.288 | 2.027 | 2.492 | 2.693 | 2.795 | 2.762 | 2.702 | 2.551 | 2.454
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.3 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 2.2 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 20 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 50 | 40 | 0
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 4.60 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 84 | M/T Maker | TECO | Turbin | 30 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PM-2203FI |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.133 | 0.234 | 0.319 | 0.427 | 0.472 | 0.505 | 0.516 | 0.524
Dis. Head | (m) | 33.9 | 32 | 28 | 24 | 16 | 12 | 8 | 4 | 2.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.093728 | 0.29013 | 0.5392 | 0.9661 | 1.1805 | 1.3513 | 1.4108
Total Head | (m) | 33.9 | 32.0937 | 28.2901 | 24.5392 | 16.9661 | 13.1805 | 9.3513 | 5.4108
Water Power | (kW) | 0 | 0.69576 | 1.079 | 1.276 | 1.1809 | 1.0141 | 0.76975 | 0.45509
Shaft Power | (kW) | 1.1012 | 1.7094 | 2.0672 | 2.252 | 2.3428 | 2.3142 | 2.2596 | 2.1286
Pump Eff. | (%) | 0 | 40.702 | 52.1972 | 56.6582 | 50.4045 | 43.8187 | 34.0658 | 21.3802
Speed | (rpm) | 3523 | 3467 | 3444 | 3427 | 3421 | 3419 | 3422 | 3432 | 3441
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.43 | 6.17 | 7.28 | 7.89 | 8.15 | 8.06 | 7.89 | 7.49 | 7.26
Motor Input | (kW) | 1.311 | 2.035 | 2.461 | 2.681 | 2.789 | 2.755 | 2.69 | 2.534 | 2.456
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.3 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 2.2 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 20 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 50 | 40 | 0
Efficiency |  | (%) | Volt.(v) | 220 | Current(A) | 8.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 84 | M/T Maker | TECO | Turbin | 30 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PM-2203FI |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification