## Datasheet
Pump Data Sheet
Model | PM-250PiS | Type | Magnet Driven Pump |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Issued Date
Item No. |  |  | Plant Name
Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
Operating Condition
liquid |  | Flow | 75ℓ/min | (Ht=5m) | Min. Con. Flow | ℓ/min
Pumping Temp. | AMB. | Suct. Press. | - | Kgf/㎠ | Design Press. | 1.2Kgf/㎠
Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 60 ℃
Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
Visc. @P.T | Cp | Total Head | 8 | m
Operating Cond. | Continuous
Construction & Performance |  |  |  |  | Material
■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | P.P+GF30%
Number of Stages | 1 Stage | Rated Power | 250 | W | Impeller | P.P+GF30%
Speed | 3450 | NPSHre | 0m |  | Shaft | Ceramics
Rotation | ■ CW □ CCW | (View From Driver) |  |  | Trust Washer | Ceramics
Bore | Size(Dia) | Rating | Face | Position | Bearing | PTFE
Suction | 25mm(1") | Kgf/㎠ |  | End | Back Casing | P.P+GF30%
Discharge | 25mm(1") | Kgf/㎠ |  | Top | O-ring | VITON
Impeller Type | OPEN | ■ Single Suct. □ Double Suct. |  | Hydrostatic
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
Mounting |  |  |  | Testing
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
Pump Driver |  |  |  |  | Spare Parts
■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 220,380V/3Φ/60Hz
Maker | WILO | Motor Fr. No.
Type | Closed | Furnished by | ■ WILO □ Customer
Power | 250w | Mounted | ■ WILO □ Customer
Pole & Speed | 2p 3450rpm | Insulation Class | □ B ■ E □ F
Accessories
□ Base Plate
□ Foundation Bolts & Nuts
□ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
□ Press. Gauge
□ Collar or Plug for Drain & Air Vent.
□ Companion Flange
□ Special Tool |  |  |  |  | Weight
Pump/Head
Driver
[5 empty] | Total Weight | 12 Kg
※ Don't run dry

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 70(5m) |  | MOTOR | OUTPUT |  |  |  | W | 250
| TOTAL HEAD | m | 8 |  |  | VOLTAGE |  |  |  | V | 220/380
| SUCTION BORE | mm | Ø | 25 |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø | 25 |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID |  |  |  |  | TYPE |  |  |  | closed
| MAKER | WILO |  |  |  | MAKER |  |  |  | WILO
[7 empty] | TYPE |  | MAGNET PUMP
[7 empty] | MODEL |  | PM-250PiS
SERVICE
SCALE:N/S
OUTLINE DRAWING
of PM TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS | [5 empty] | Q'TY
|  | KS | DIN | AISI
10 | CASING | PolyPropylene | [5 empty] | 1
20 | IMPELLER ASSY | PolyPropylene+Ferrite | [5 empty] | 1
30 | WASHER | Aℓ2O3 | [5 empty] | 2
40 | SHAFT, PUMP | Aℓ2O3 | [5 empty] | 1
50 | O-RING | VITON | [5 empty] | 1
60 | CASING, BACK | PolyPropylene | [5 empty] | 1
70 | MOTOR ASSY | - | [5 empty] | 1
80 | NUT | SMC440 | 42CrMo4 | 4140 |  |  |  | 1
90 | MAGNET ASSY | AℓDC+Ferrite | [5 empty] | 1
100 | SCREW, SPECIAL | STS304 | X5CrNi189 | 304 |  |  |  | 6
|  |  |  | TYPE |  | MAGNET PUMP
|  |  |  | MODEL |  | PM-250PiS
SERVICE
|  |  |  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PM TYPE
90
80
70
60
50
10
20
30
40
100

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 44 | 54 | 63 | 71 | 79 | 86 | 90
Dis. Head | (m) | 10.7 | 9 | 8 | 7 | 6 | 5 | 4 | 3.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 10.7 | 9 | 8 | 7 | 6 | 5 | 4 | 3.5
Water Power | (㎾) | 0 | 0.064548 | 0.070416 | 0.071883 | 0.069438 | 0.064385 | 0.056072 | 0.051345
Shaft Power | (㎾) | 0.1332 | 0.1776 | 0.1884 | 0.1962 | 0.2028 | 0.2112 | 0.2172 | 0.2214
Pump Eff. | (%) | 0 | 36.3446 | 37.3758 | 36.6376 | 34.2396 | 30.4853 | 25.8158 | 23.1911
Speed | (rpm) | 3510 | 3474 | 3463 | 3455 | 3446 | 3443 | 3434 | 3432
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 0.74 | 0.79 | 0.81 | 0.81 | 0.82 | 0.85 | 0.85 | 0.86
Motor Input | (㎾) | 0.222 | 0.296 | 0.314 | 0.327 | 0.338 | 0.352 | 0.362 | 0.369
Motor Eff. | (%) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 75 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.25 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 5 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 26 | 26
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 60 | Maker | WILO | Turbin | 25 | 23
Item No. |  |  | Serial No. |  | Inspector | S.G.S | Run (Hr) | B/R (℃) | Test Date
Model | PM-250PI |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification