## Datasheet
PUMP DATA SHEET | [8 empty] | CUSTOMER
ITEM No.
DATE
Model |  | PM-Series |  |  | Title |  |  |  | Sheet No.
Location |  |  |  |  | Plant Name
Agent No. |  |  |  |  | Quantity
Service | [8 empty] | Location |  | ■ In, □ Out
OPERATING CONDITION
Pumping Temp. |  | Ambient |  | Design Temp. |  | 60℃ |  |  | Altitude |  | 1,000m max
Sp.Gr.@P.T |  | Below 1.05 |  | Operating Condition |  | Continuous |  |  | Kinematic viscosity |  | equivalent to water
Vap.Press.@P.T |  | kgf/㎠A |  | Humidity |  | 95% max.
Visc.@P.T |  | Below 30Cp |  | Liquid
PERFORMANCE AND CONSTRUCTIONS
|  | Model | PM-403PI PM-403PN | PM-753PI PM-753PN | PM-1503PI PM-1503PN | PM-2203PI PM-2203PN | PM-3703PI PM-3703PN | PM-403FI PM-403FN | PM-753FI PM-753FN | PM-1503FI PM-1503FN | PM-2203FI PM-2203FN | PM-3703FI PM-3703FN
Classification
Output(kW) |  |  | 0.37 | 0.75 | 1.5 | 2.2 | 3.7 | 0.37 | 0.75 | 1.5 | 2.2 | 3.7
Input(kW) |  |  | 0.53 | 0.99 | 1.6 | 2.7 | 3 | 0.53 | 0.99 | 1.6 | 2.7 | 3
Current (A) | 3 Phase | 220V | 1.5 | 2.9 | 5.39 | 7.95 | 12.6 | 1.5 | 2.9 | 5.39 | 7.95 | 12.6
|  | 380V | 0.87 | 1.68 | 3.12 | 4.6 | 7.29 | 0.87 | 1.68 | 3.12 | 4.6 | 7.29
|  | 440V | 0.75 | 1.45 | 2.69 | 3.98 | 6.3 | 0.75 | 1.45 | 2.69 | 3.98 | 6.3
Flow (l/min) | Rated Flow | Q | 100 | 180 | 230 | 300 | 300 | 100 | 180 | 230 | 300 | 300
|  | at H(m) | 8 | 12 | 20 | 20 | 25 | 8 | 12 | 20 | 20 | 25
| Max. Flow |  | 250 | 350 | 450 | 480 | 580 | 250 | 350 | 450 | 480 | 580
Shut off Head(m) |  |  | 9 | 16 | 25 | 30 | 35 | 9 | 16 | 25 | 30 | 35
Piping(mm) |  | Suct. | 40 |  | 50 |  | 50 | 40 |  | 50 |  | 50
|  | Disch. | 40 |  | 40 |  | 50 | 40 |  | 40 |  | 50
Motor (V/Phase/Hz) |  |  | I : 220/380V 3Phase 60Hz N : 440V 3Phase 60Hz
Motor Frame Size |  |  | 71 | 80 | 90L | 90L | 112M | 71 | 80 | 90L | 90L | 112M
Motor Efficiency |  |  | 76 | 77.5 | 83.5 | 84 | 86.5 | 76 | 77.5 | 83.5 | 84 | 86.5
Bearing | Pump Side |  | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ
| Fan Side |  | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ | 6202ZZ | 6204ZZ | 6205ZZ | 6205ZZ | 6306ZZ
Diameter of Impeller(mm) |  |  | 82 | 99 | 124 | 140 | 139 | 82 | 99 | 124 | 140 | 139
Impeller Type |  |  | Centrifugal Closed Impeller
Flow Direction |  |  | ■ Radial, □ Mixed, □ Axial
Weight (kg) | Pump/Head |  | 7 | 13.5 | 15 | 14.5 | 21.5 | 7.5 | 14.5 | 16 | 15.5 | 23
| Driver(Motor) |  | 13 | 17 | 25 | 28 | 47 | 13 | 17 | 25 | 28 | 47
| Net Weight |  | 20 | 30.5 | 40 | 42.5 | 68.5 | 20.5 | 31.5 | 41 | 43.5 | 70
| Gross Weight |  | 21.5 | 32.5 | 41.5 | 44.5 | 74 | 22 | 33.5 | 43 | 45.5 | 75.5
Material | Casing |  | P.P+G/F30% |  |  |  |  | PVdF
| Mouth Washer |  | Ceramic
| Impeller |  | P.P+G/F30% |  |  |  |  | PVdF
| I/P Mouth Ring |  | PTFE (Teflon)
| I/P Bearing |  | PTFE (Teflon)
| Shaft |  | Ceramic
| Rear Casing |  | P.P+G/F30% |  |  |  |  | PVdF
| O-Ring |  | Viton
| Magnet |  | Ferrite |  | NFb |  |  | Ferrite |  | NFb
| Base Plate |  | P.P+G/F30%
PUMP DRIVER
Mounting Position |  |  | ■ Hotizontal, □ Vertical |  |  | Motor Type |  | TEFC
Motor Maker |  |  | TECO (in TAIWAN) |  |  | Insulation Class |  | E
Shaft Seal |  |  | □ G/Packing, □ M/Seal, ■ None |  |  | Protecting Index |  | IP54
Pole & Speed |  |  | 2 pole / 3,450 rpm |  |  | Rotation |  | □ CW, ■ CCW (viewed from pump Head)
Motor Bearing Lubrication |  |  | ■ Grease, □ Oil Bath |  |  | Cooling |  | □ Stuff. Box, □ B/R Housing, ■ Fan cooling
TESTING | [6 empty] | HYDROSTATIC
( Items ) |  |  | ( Self test ) |  | ( Witness ) |  | Casing | 150% of Shut-Off Head |  |  |  | 3 min.
Run Performal |  |  | ■ Yes, □ No |  | □ Yes, ■ No |  | Bracket
Hydrostatic |  |  | ■ Yes, □ No |  | □ Yes, ■ No
ACCESSORIES
■ Base plate |  | □ Drain Rim |  | □ Foundation Bolts & Nuts |  |  | ■ Plug for Priming & Air Vent
Coupling |  | □ Sun Flex □ Woods □ Grid ■ No |  |  |  |  | □ Sealing Flushing Pipe □ Cooling Popin ■ No
Press. Gauge |  | □ Suct. Vacuum □ Suct. Compound □ Suct. Press □ Disch. Press ■ No
□ Companion Flange
□ Special Tools
SPARE PARTS
Impeller |  | Set(S) |  | O-Ring |  | Set(S) |  | Flange Socket |  | Set(S)
Bearing |  | Set(S) |  | Driver Magnet |  | Set(S) |  | Pump Bracket |  | Set(S)
Casing |  | Set(S) |  | Base Plate |  | Set(S) |  | Motor Assembly |  | Set(S)
Rear Casing |  | Set(S) |  | Flange |  | Set(S) |  | Set(S) |  | Set(S)
Do Not Dry Running!

## Outline Drawing
|  |  |  | OUTLINE DRAWING of PM-SERIES | [6 empty] | CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | TYPE |  |  | MAGNET DRIVEN |  |  |  | MOTOR | VOLTAGE |  |  |  |  | 220/380V or 440V
| INSTALLATION |  |  | INDOOR |  |  |  |  | FREQUENCY |  |  |  |  | 60Hz
| PIPING |  |  | FLANGE TYPE |  |  |  |  | No. of REVOLUTION |  |  |  |  | 3400 r.p.m
| LIQUID |  |  | FLUID |  |  |  |  | TYPE |  |  |  |  | TEFC
| MAKER |  |  | TRUNDEAN(TAIWAN) |  |  |  |  | MAKER |  |  |  |  | TECO (TAIWAN)
Model |  | Power |  | Output | Dimension (mm) | [9 empty] | Piping(mm) |  | Weight | Gross Weight
|  | (V) | (ph) | (W) | H | H1 | H2 | L | L 1 | L 2 | B1 | B2 | B3 | W | Suc. | Disch. | (Kg)
PM-403PI/FI |  | 220/380 | 3 | 370 | 235 | 110 | 125 | 470 | 86 | 52 | 98 | 140 | 110 | 140 | 40 | 40 | 20.0/20.5 | 24
PM-403PN/FN |  | 440 |  |  |  | 90 | 104 |  | 252 | 98.1 | 157.5 | 51 | 120 |  | 1"¼ | 1"
PM-753PI/FI |  | 220/380 | 3 | 750 | 255 | 115 | 140 | 525 | 90 | 66 | 130 | 165 | 130 | 160 |  |  | 30.5/31.5 | 35
PM-753PN/FN |  | 440
PM-1503PI/FI |  | 220/380 | 3 | 1500 | 275 | 115 | 160 | 620 | 100 | 66 | 200 | 165 | 210 | 260 | 50 | 40 | 40.0/41.0
PM-1503PN/FN |  | 440 | [15 empty] | 45
PM-2203PI/FI |  | 220/380 | 3 | 2200 | [12 empty] | 42.5/43.5 | 48
PM-2203PN/FN |  | 440
PM-3703PI/FI |  | 220/380 | 3 | 3700 | 315 | 165 | 150 | 685 | 100 | 66 | 90 | 180 | 200 | 240 | 50 | 50 | 68.5/70.0
PM-3703PN/FN |  | 440
[10 empty] | TYPE |  |  | MAGNET PUMP
[10 empty] | MODEL |  |  | PM-Series
SERVICE
[10 empty] | SCALE |  |  | N/S

## Sectional Drawing
|  | SECTIONAL DRAWING of PM-SERIES |  |  | CUSTOMER
ITEM No.
DATE
NO | PART NAME |  | MATERIAL |  |  |  | Q'TY
|  |  | PM-403PI PM-753PI | PM-1503PI | PM-403FI PM-753FI | PM-1503FI
|  |  |  | PM-2203PI |  | PM-2203FI
|  |  |  | PM-3703PI |  | PM-3703FI
1 | FLANGE SOCKET |  | PP+G/F30% |  | PVdF |  | 1
2 | O-RING |  | VITON |  |  |  | 1
3 | FLANGE |  | NYLON |  |  |  | 1
4 | BOLT |  | STS304 |  |  |  | 8
5 | FRONT CASING |  | PP+G/F30% |  | PVdF |  | 1
6 | CASING MOUTH RING |  | CERAMIC (Al2O3) |  |  |  | 1
7 | IMPELLER |  | PP+G/F30% |  | PVdF |  | 1
8 | IMPELLER MOUTH RING |  | PTFE(TEFLON) |  |  |  | 1
9 | O-RING IN CASING |  | VITON |  |  |  | 1
10 | REAR CASING |  | PP+G/F30% |  | PVdF |  | 1
11 | SHAFT |  | CERAMIC (Al2O3) |  |  |  | 1
12 | BEARING |  | PTFE(TEFLON) |  |  |  | 1
13 | MAGNET |  | FERRITE | NFb | FERRITE | NFb | 1
14 | BEARING WASHER |  | CERAMIC (Al2O3) |  |  |  | 1
15 | MAGNET HOUSING |  | GC250 |  |  |  | 1
16 | PUMP BRACKET |  | GC250 |  |  |  | 1
17 | PUMP BASE PLATE |  | PP+G/F30% |  |  |  | 1
18 | MOTOR |  | 3PHASE 220/380V or 440V 60Hz TEFC (TECO) |  |  |  | 1
[5 empty] | TYPE | MAGNET PUMP
[5 empty] | MODEL | PM-Series
SERVICE
[5 empty] | SCALE | N/S

## Test Report(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.105 | 0.19 | 0.258 | 0.32 | 0.393
Dis. Head | (m) | 16.6 | 15 | 12 | 9 | 6 | 1.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 16.6 | 15 | 12 | 9 | 6 | 1.4
Water Power | (kW) | 0 | 0.25672 | 0.37164 | 0.37849 | 0.31296 | 0.089683
Shaft Power | (kW) | 0.39215 | 0.5921 | 0.69983 | 0.74013 | 0.74555 | 0.713
Pump Eff. | (%) | 0 | 43.3584 | 53.1047 | 51.1381 | 41.9771 | 12.5782
Speed | (rpm) | 3493 | 3423 | 3387 | 3373 | 3367 | 3384
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.67 | 2.29 | 2.65 | 2.81 | 2.82 | 2.7
Motor Input | (kW) | 0.506 | 0.764 | 0.903 | 0.955 | 0.962 | 0.92
Motor Eff. | (%) | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.18 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 0.75 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 12 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 40 | 40
Efficiency |  | (%) | Volt.(v) | 220 | Current(A) |  | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77.5 | M/T Maker | TECO | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.H.W | Run (Hr) | B/R (℃) | Test Date
Model | PM-753 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
-5%일때의 Data |  | 15.77 | 14.25 | 11.4 | 8.55 | 5.7 | 1.33
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.11 | 0.142 | 0.196 | 0.243 | 0.302 | 0.334 | 0.373
Dis. Head | (m) | 16.8 | 15 | 14 | 12 | 10 | 7 | 5 | 2.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Head | (m) | 16.8 | 15 | 14 | 12 | 10 | 7 | 5 | 2.2
Water Power | (kW) | 0 | 0.26895 | 0.32404 | 0.38338 | 0.39609 | 0.34458 | 0.27221 | 0.13376
Shaft Power | (kW) | 0.3875 | 0.6076 | 0.65643 | 0.71998 | 0.7533 | 0.76802 | 0.77035 | 0.75485
Pump Eff. | (%) | 0 | 44.2643 | 49.365 | 53.2485 | 52.5806 | 44.866 | 35.3359 | 17.7198
Speed | (rpm) | 3519 | 3461 | 3448 | 3431 | 3415 | 3408 | 3406 | 3407
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.02 | 1.39 | 1.48 | 1.6 | 1.66 | 1.68 | 1.69 | 1.66
Motor Input | (kW) | 0.5 | 0.784 | 0.847 | 0.929 | 0.972 | 0.991 | 0.994 | 0.974
Motor Eff. | (%) | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5 | 77.5
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.18 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 0.75 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 12 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 | 40 | 40 | 0
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 1.68 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77.5 | M/T Maker | TECO | Turbin | 20 | 17
Item No. |  |  | Serial No. |  | Inspector | S.H.W | Run (Hr) | B/R (℃) | Test Date
Model | PM-753 |  | Customer |  |  |  | 2 | 36
Checked By |  |  |  |  | Approved By
Vacuum | mmhg
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
-5%일때의 Data |  | 15.96 | 14.25 | 13.3 | 11.4 | 9.5 | 6.65
0 | 0.11 | 0.142 | 0.196 | 0.243 | 0.302 | 0.334 | 0.373
0 | 110 | 142 | 196 | 243 | 302 | 334 | 373
16.8 | 15 | 14 | 12 | 10 | 7 | 5 | 2.2
3519 | 3461 | 3448 | 3431 | 3415 | 3408 | 3406 | 3407
500 | 784 | 847 | 929 | 972 | 991 | 994 | 974
0.5 | 0.784 | 0.847 | 0.929 | 0.972 | 0.991 | 0.994 | 0.974
1.02 | 1.39 | 1.48 | 1.6 | 1.66 | 1.68 | 1.69 | 1.66
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification