## Datasheet(PSB-1012HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-1012HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 80 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 12 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 416 | mm | Pump | 3 | kg
37 | Motor | 295 | mm | Motor | 10.6 | kg
38 | Total | 711 | mm | Total | 13.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-1033HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-1033HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 80 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 416 | mm | Pump | 3 | kg
37 | Motor | 265 | mm | Motor | 8.3 | kg
38 | Total | 681 | mm | Total | 11.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-2012HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2012HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 125 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 555 | mm | Pump | 4.3 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 930 | mm | Total | 18.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-2032HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2032HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 125 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 555 | mm | Pump | 4.3 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 895 | mm | Total | 15.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-2033HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2033HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 125 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 5.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 555 | mm | Pump | 4.3 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 895 | mm | Total | 15.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-3012HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-3012HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 165 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 685 | mm | Pump | 5.5 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 1115 | mm | Total | 21.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-3032HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-3032HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 165 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 12.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 685 | mm | Pump | 5.5 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 1060 | mm | Total | 19.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-3033HP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-3033HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 165 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 7.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 685 | mm | Pump | 5.5 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 1060 | mm | Total | 19.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-5532H)
Submersible Motor Pump Data Sheet
1 | Model | PSB-5532H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Shaft | STS410
10 | Rated Capacity | 70 | ℓ/min | Shell | STS304
11 | Shut off Head | 260 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 20.8 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 662 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 28 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 980 | mm | Pump | 8.9 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1535 | mm | Total | 32.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-5533H)
Submersible Motor Pump Data Sheet
1 | Model | PSB-5533H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Shaft | STS410
10 | Rated Capacity | 70 | ℓ/min | Shell | STS304
11 | Shut off Head | 260 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 12 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 662 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 28 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 980 | mm | Pump | 8.9 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1535 | mm | Total | 32.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB4-7532H)
Submersible Motor Pump Data Sheet
1 | Model | PSB4-7532H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 230 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 360 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 30 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 662 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 37 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1250 | mm | Pump | 10.5 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1925 | mm | Total | 39.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB4-7533H)
Submersible Motor Pump Data Sheet
1 | Model | PSB4-7533H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 230 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 360 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 17.3 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 662 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 37 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1250 | mm | Pump | 10.5 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1925 | mm | Total | 39.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PSB-1012GP | 14 |  |  | 1 |  | 1 |  | 220 | 60
PSB-1012HP | 8 |  |  | 1 |  | 1 |  | 220 | 60
PSB-1033GP | 14 |  |  | 1 |  | 3 |  | 380 | 60
PSB-1033HP | 8 |  |  | 1 |  | 3 |  | 380 | 60
PSB-2012GP | 24 |  |  | 2 |  | 1 |  | 220 | 60
PSB-2012HP | 13 | 28 |  | 2 |  | 1 |  | 220 | 60
PSB-2032GP | 24 | 28 |  | 2 |  | 3 |  | 220 | 60
PSB-2032HP | 13 | 37 |  | 2 |  | 3 |  | 220 | 60
PSB-2033GP | 24 | 37 |  | 2 |  | 3 |  | 380 | 60
PSB-2033HP | 13 |  |  | 2 |  | 3 |  | 380 | 60
PSB-3012HP | 17 | 28 |  | 3 |  | 1 |  | 220 | 60
PSB-3032HP | 17 | 28 |  | 3 |  | 3 |  | 220 | 60
PSB-3033HP | 17 | 37 |  | 3 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PSB-1012GP | 520 |  |  | 295 |  |  | 815
PSB-1012HP | 416 |  |  | 295 |  |  | 711
PSB-1033GP | 520 |  |  | 265 |  |  | 785
PSB-1033HP | 416 |  |  | 265 |  |  | 681
PSB-2012GP | 774 |  |  | 375 |  |  | 1149
PSB-2012HP | 555 | 28 |  | 375 |  |  | 930
PSB-2032GP | 774 | 28 |  | 340 |  |  | 1114
PSB-2032HP | 555 | 37 |  | 340 |  |  | 895
PSB-2033GP | 774 | 37 |  | 340 |  |  | 1114
PSB-2033HP | 555 |  |  | 340 |  |  | 895
PSB-3012HP | 685 | 28 |  | 430 |  |  | 1115
PSB-3032HP | 685 | 28 |  | 375 |  |  | 1060
PSB-3033HP | 685 | 37 |  | 375 |  |  | 1060
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PSB-1012GP | 4.5 |  |  | 10.6 |  |  | 15.1
PSB-1012HP | 3 |  |  | 10.6 |  |  | 13.6
PSB-1033GP | 4.5 |  |  | 8.3 |  |  | 12.8
PSB-1033HP | 3 |  |  | 8.3 |  |  | 11.3
PSB-2012GP | 6 |  |  | 14 |  |  | 20
PSB-2012HP | 4.3 | 28 |  | 14 |  |  | 18.3
PSB-2032GP | 6 | 28 |  | 11.4 |  |  | 17.4
PSB-2032HP | 4.3 | 37 |  | 11.4 |  |  | 15.7
PSB-2033GP | 6 | 37 |  | 11.4 |  |  | 17.4
PSB-2033HP | 4.3 |  |  | 11.4 |  |  | 15.7
PSB-3012HP | 5.5 | 28 |  | 16.4 |  |  | 21.9
PSB-3032HP | 5.5 | 28 |  | 14.2 |  |  | 19.7
PSB-3033HP | 5.5 | 37 |  | 14.2 |  |  | 19.7
※MOTOR MAKER : SUMOTO s.r.l.
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PSB-GP,HP TYPE
104mm
P.L
M.L
T.L
Cable Guard
Included

## Outline Drawing (2)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE | VOLTS | HZ
PSB-5532H | 28 | 28 |  | 5 |  | 3 | 220 | 60
PSB-5533H | 28 | 28 |  | 5 |  | 3 | 380 | 60
PSB4-7532H | 37 | 37 |  | 7.5 |  | 3 | 220 | 60
PSB4-7533H | 37 | 37 |  | 7.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PSB-5532H | 980 |  |  | 555 |  |  | 1535
PSB-5533H | 980 |  |  | 555 |  |  | 1535
PSB4-7532H | 1250 |  |  | 675 |  |  | 1925
PSB4-7533H | 1250 |  |  | 675 |  |  | 1925
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PSB-5532H | 8.9 |  |  | 23.4 |  |  | 32.3
PSB-5533H | 8.9 |  |  | 23.4 |  |  | 32.3
PSB4-7532H | 10.5 |  |  | 29.4 |  |  | 39.9
PSB4-7533H | 10.5 |  |  | 29.4 |  |  | 39.9
※MOTOR MAKER : SUMOTO s.r.l.
※DISCHARGE DIA. : 32mm
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PSB-G,H TYPE
104mm
P.L
M.L
T.L
Cable Guard
Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | POM + BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | DIFFUSER |  |  | NORYL |  | Stages
9 | SLIDING BEARING |  |  | NBR |  | Stages
10 | UPTHRUST WASHER |  |  | STS304 |  | Stages
11 | MIDDLE CASING |  |  | NORYL |  | Stages
12 | IMPELLER |  |  | NORYL+STS304 |  | Stages
13 | IMPELLER GASKET |  |  | NBR |  | Stages
14 | MIDDLE SPACER |  |  | NORYL |  | 1~2
15 | SLEEVE |  |  | STS304 |  | 1~2
16 | SLIDING BEARING |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | LOWER SPACER |  |  | NORYL |  | 1
19 | SHAFT |  |  | STS410 |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | BASE |  |  | NORYL |  | 1
24 | SCREW |  |  | STS304 |  | 1
25 | CABLE GUARD |  |  | HD PE |  | 1
26 | STRAINER |  |  | STS304 |  | 1
27 | SCREW |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PSB-GP,HP TYPE
22
27
26
23
24
25
13
20
21
18
16
15
14
12
3
19
17
7
11
10
8
9
5
6
4
1
2

## Sectional Drawing (2)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | SLEEVE |  |  | STS304 |  | 1
9 | DIFFUSER |  |  | NORYL |  | Stages
10 | SLIDING BEARING |  |  | NBR |  | Stages
11 | UPTHRUST WASHER |  |  | STS304 |  | Stages
12 | MIDDLE CASING |  |  | NORYL |  | Stages
13 | IMPELLER |  |  | NORYL+STS304 |  | Stages
14 | IMPELLER GASKET |  |  | NBR |  | Stages
15 | MIDDLE SPACER |  |  | NORYL |  | 1~2
16 | SLEEVE |  |  | STS304 |  | 1~2
17 | SLIDING BEARING |  |  | NBR |  | 1~2
18 | SHELL |  |  | STS304 |  | 1
19 | LOWER SPACER |  |  | NORYL |  | 1
20 | SHAFT |  |  | STS410 |  | 1
21 | COUPLING |  |  | STS304 |  | 1
22 | SCREW |  |  | STS304 |  | 1
23 | STOP RING |  |  | STS304 |  | 1
24 | BASE |  |  | BRASS |  | 1
25 | STRAINER |  |  | STS304 |  | 1
26 | SCREW |  |  | STS304 |  | 6
27 | CABLE GUARD |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PSB-G,H TYPE
13
25
24
26
21
23
22
12
19
14
20
18
27
7
11
16
17
15
9
10
8
6
5
4
3
2
1

## Tset Report(PSB-1012HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 35 | 60 | 80 | 100 | 106 | 127
Dis. Head | (m) | 80.7 | 76.8 | 73.2 | 64.9 | 50.1 | 30.5 | 24 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.026841 | 0.078879 | 0.14023 | 0.21911 | 0.24619 | 0.3534
Total Head | (m) | 81.7 | 77.8088 | 74.2268 | 65.9789 | 51.2402 | 31.7191 | 25.2462 | 1.4534
Water Power | (㎾) | 0 | 0.25366 | 0.42346 | 0.64527 | 0.66817 | 0.51702 | 0.4362 | 0.030087
Shaft Power | (㎾) | 0.68853 | 0.83426 | 0.9381 | 1.1092 | 1.1983 | 1.2184 | 1.2219 | 1.2048
Pump Eff. | (%) | 0 | 30.405 | 45.1406 | 58.1747 | 55.7605 | 42.4362 | 35.6991 | 2.4973
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.94 | 8.79 | 9.48 | 10.66 | 11.27 | 11.39 | 11.41 | 11.29
Motor Input | (㎾) | 1.167 | 1.414 | 1.59 | 1.88 | 2.031 | 2.065 | 2.071 | 2.042
Motor Eff. | (%) | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 12 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 59 | Maker | Sumoto | Turbin | 21 | 20
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-1012HP |  | Customer |  |  |  | 0.5 |  | 2013.11.8
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-2012HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 120 | 137
Dis. Head | (m) | 127 | 115 | 104 | 85 | 62 | 35 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.41124
Total Head | (m) | 127.75 | 115.7697 | 104.8289 | 85.8902 | 62.9691 | 36.0655 | 4.1612
Water Power | (㎾) | 0 | 0.56611 | 1.0252 | 1.12 | 1.0264 | 0.70544 | 0.092925
Shaft Power | (㎾) | 0.92752 | 1.4137 | 1.651 | 1.7333 | 1.7068 | 1.6449 | 1.5803
Pump Eff. | (%) | 0 | 40.0443 | 62.0958 | 64.6164 | 60.1357 | 42.8861 | 5.8801
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.83 | 11.15 | 12.83 | 13.45 | 13.23 | 12.75 | 12.27
Motor Input | (㎾) | 1.364 | 2.079 | 2.428 | 2.549 | 2.51 | 2.419 | 2.324
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.75
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 15 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2012HP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-2032HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 130 | 149
Dis. Head | (m) | 125 | 114 | 105 | 90 | 70 | 32 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.37029 | 0.48644
Total Head | (m) | 125.7 | 114.7197 | 105.7789 | 90.8402 | 70.9191 | 33.0703 | 1.1864
Water Power | (㎾) | 0 | 0.56098 | 1.0345 | 1.1846 | 1.156 | 0.70076 | 0.028815
Shaft Power | (㎾) | 1.0074 | 1.3892 | 1.641 | 1.7498 | 1.7841 | 1.7308 | 1.6644
Pump Eff. | (%) | 0 | 40.3818 | 63.0404 | 67.6963 | 64.7928 | 40.4869 | 1.7313
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.15 | 6.21 | 6.99 | 7.34 | 7.47 | 7.32 | 7.1
Motor Input | (㎾) | 1.38 | 1.903 | 2.248 | 2.397 | 2.444 | 2.371 | 2.28
Motor Eff. | (%) | 73 | 73 | 73 | 73 | 73 | 73 | 73
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2032HP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-2033HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 130 | 150
Dis. Head | (m) | 125 | 115 | 106 | 92 | 73 | 35 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.37029 | 0.49299
Total Head | (m) | 125.7 | 115.7197 | 106.7789 | 92.8402 | 73.9191 | 36.0703 | 1.193
Water Power | (㎾) | 0 | 0.56587 | 1.0443 | 1.2106 | 1.2049 | 0.76433 | 0.029169
Shaft Power | (㎾) | 1.0293 | 1.4162 | 1.6717 | 1.7666 | 1.8031 | 1.752 | 1.7009
Pump Eff. | (%) | 0 | 39.9569 | 62.4692 | 68.5292 | 66.8228 | 43.6261 | 1.7149
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.19 | 3.78 | 4.2 | 4.37 | 4.46 | 4.39 | 4.32
Motor Input | (㎾) | 1.41 | 1.94 | 2.29 | 2.42 | 2.47 | 2.4 | 2.33
Motor Eff. | (%) | 73 | 73 | 73 | 73 | 73 | 73 | 73
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 5.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2033HP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-3012HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 31 | 60 | 80 | 114 | 140
Dis. Head | (m) | 165 | 150 | 134.5 | 112.5 | 60 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021056 | 0.078879 | 0.14023 | 0.28475 | 0.42945
Total Head | (m) | 165.7 | 150.7211 | 135.2789 | 113.3402 | 60.9848 | 1.1295
Water Power | (㎾) | 0 | 0.76159 | 1.323 | 1.478 | 1.1332 | 0.025774
Shaft Power | (㎾) | 1.3797 | 1.9439 | 2.2722 | 2.3681 | 2.3156 | 2.1693
Pump Eff. | (%) | 0 | 39.1786 | 58.2267 | 62.4111 | 48.9384 | 1.1881
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 9.5 | 13.29 | 15.6 | 16.25 | 15.92 | 14.89
Motor Input | (㎾) | 1.971 | 2.777 | 3.246 | 3.383 | 3.308 | 3.099
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-3012HP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-3032HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 120 | 135
Dis. Head | (m) | 169 | 153 | 133 | 110 | 80 | 43 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.39933
Total Head | (m) | 169.7 | 153.7197 | 133.7789 | 110.8402 | 80.9191 | 44.0155 | 5.0993
Water Power | (㎾) | 0 | 0.75169 | 1.3084 | 1.4454 | 1.319 | 0.86094 | 0.11221
Shaft Power | (㎾) | 1.3202 | 1.9085 | 2.2548 | 2.3169 | 2.3206 | 2.2274 | 2.1364
Pump Eff. | (%) | 0 | 39.3872 | 58.0259 | 62.3821 | 56.837 | 38.6524 | 5.2524
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.94 | 8.51 | 9.6 | 9.83 | 9.9 | 9.49 | 9.23
Motor Input | (㎾) | 1.784 | 2.579 | 3.047 | 3.131 | 3.136 | 3.01 | 2.887
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 12.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-3032HP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-3033HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 120 | 138
Dis. Head | (m) | 167 | 153 | 136.5 | 114 | 82 | 42 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.41727
Total Head | (m) | 167.7 | 153.7197 | 137.2789 | 114.8402 | 82.9191 | 43.0155 | 1.1173
Water Power | (㎾) | 0 | 0.75169 | 1.3426 | 1.4975 | 1.3516 | 0.84138 | 0.025132
Shaft Power | (㎾) | 1.3394 | 1.9166 | 2.257 | 2.3458 | 2.3532 | 2.2718 | 2.2052
Pump Eff. | (%) | 0 | 39.2199 | 59.4855 | 63.8382 | 57.4359 | 37.036 | 1.1397
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.43 | 5.25 | 5.84 | 5.98 | 5.99 | 5.87 | 5.76
Motor Input | (㎾) | 1.81 | 2.59 | 3.05 | 3.17 | 3.18 | 3.07 | 2.98
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 7.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-3033HP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-5532H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 90 | 120 | 140 | 150
Dis. Head | (m) | 267 | 252 | 230 | 195 | 118.3 | 50 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.17748 | 0.31552 | 0.42945 | 0.49299
Total Head | (m) | 267.65 | 252.6697 | 230.7289 | 195.8275 | 119.2655 | 51.0795 | 1.143
Water Power | (㎾) | 0 | 1.2356 | 2.2565 | 2.8728 | 2.3328 | 1.1656 | 0.027946
Shaft Power | (㎾) | 2.4472 | 3.192 | 3.762 | 4.0584 | 4.104 | 3.99 | 3.7696
Pump Eff. | (%) | 0 | 38.7079 | 59.9821 | 70.7862 | 56.8429 | 29.2139 | 0.74136
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 13.05 | 14.43 | 16.58 | 17.54 | 17.72 | 17.31 | 16.59
Motor Input | (㎾) | 3.22 | 4.2 | 4.95 | 5.34 | 5.4 | 5.25 | 4.96
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 70 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.65
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 20.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-5532H |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-5533H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 48 | 80 | 109 | 123 | 141
Dis. Head | (m) | 273 | 235 | 190 | 120 | 80 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.050483 | 0.14023 | 0.26032 | 0.33149 | 0.43561
Total Head | (m) | 273.65 | 235.7005 | 190.7902 | 120.9103 | 80.9815 | 6.0856
Water Power | (㎾) | 0 | 1.8441 | 2.4879 | 2.1482 | 1.6236 | 0.13987
Shaft Power | (㎾) | 2.4016 | 3.6024 | 3.8608 | 3.8152 | 3.7012 | 3.61
Pump Eff. | (%) | 0 | 51.1914 | 64.4401 | 56.3067 | 43.8668 | 3.8744
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.23 | 9.07 | 9.51 | 9.35 | 9.18 | 9
Motor Input | (㎾) | 3.16 | 4.74 | 5.08 | 5.02 | 4.87 | 4.75
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 70 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.65
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 12 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-5533H |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB4-7532H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 38 | 60 | 80 | 100 | 120 | 136
Dis. Head | (m) | 367 | 330 | 298 | 242 | 172 | 90 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.031639 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.40526
Total Head | (m) | 367.7 | 330.7316 | 298.7789 | 242.8402 | 172.9191 | 91.0155 | 4.1053
Water Power | (㎾) | 0 | 2.0486 | 2.9221 | 3.1666 | 2.8186 | 1.7803 | 0.091005
Shaft Power | (㎾) | 3.1031 | 4.5507 | 5.082 | 5.3053 | 5.3207 | 5.0127 | 4.6816
Pump Eff. | (%) | 0 | 45.0162 | 57.4982 | 59.6882 | 52.9739 | 35.5151 | 1.9439
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 16.27 | 19.84 | 21.41 | 22.11 | 22.16 | 21.22 | 19.99
Motor Input | (㎾) | 4.03 | 5.91 | 6.6 | 6.89 | 6.91 | 6.51 | 6.08
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 230 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 30 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB4-7532H |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB4-7533H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 41 | 60 | 80 | 100 | 120 | 137
Dis. Head | (m) | 362 | 325 | 290 | 237 | 168 | 90 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.036832 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.41124
Total Head | (m) | 362.7 | 325.7368 | 290.7789 | 237.8402 | 168.9191 | 91.0155 | 4.1112
Water Power | (㎾) | 0 | 2.1769 | 2.8438 | 3.1014 | 2.7534 | 1.7803 | 0.091808
Shaft Power | (㎾) | 3.1493 | 4.7047 | 5.0743 | 5.3053 | 5.313 | 5.0743 | 4.697
Pump Eff. | (%) | 0 | 46.2707 | 56.0435 | 58.4592 | 51.8235 | 35.0839 | 1.9546
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.58 | 12.5 | 13.01 | 13.37 | 13.43 | 12.96 | 12.58
Motor Input | (㎾) | 4.09 | 6.11 | 6.59 | 6.89 | 6.9 | 6.59 | 6.1
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 230 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 17.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB4-7533H |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification