## Datasheet(1-22)
Submersible Motor Pump Data Sheet
1 | Model | PSS-1-22_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Discharge Piece | STS304
10 | Rated Capacity | 20 | ℓ/min | Impeller | STS304
11 | Shut off Head | 180 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 40 | % | Pump Shaft | STS431
14 | Min. Flow | 10 | ℓ/min | Coupling | STS304
15 | Max. Flow | 25 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 22 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 629 | mm | Pump | 5.1 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 927 | mm | Total | 16 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-1-13 | MF4-1012 | 13 |  |  | 1 |  | 1 | 220 | 60
| MF4-1033 | [5 empty] | 3 | 380
PSS-1-18 | MF4-1012 | 18 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-1-22 | MF4-1012 | 22 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-1-26 | MF4-1512 | 26 |  |  | 1.5 |  | 1 | 220
| MF4-1533 | [5 empty] | 3 | 380
PSS-1-31 | MF4-1512 | 31 |  |  | 1.5 |  | 1 | 220
| MF4-1533 | [5 empty] | 3 | 380
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-1-13 | MF4-1012 | 440 |  |  | 298 |  |  | 738
| MF4-1033 | 440 |  |  | 298 |  |  | 738
PSS-1-18 | MF4-1012 | 545 |  |  | 298 |  |  | 843
| MF4-1033 | 545 |  |  | 298 |  |  | 843
PSS-1-22 | MF4-1012 | 629 |  |  | 298 |  |  | 927
| MF4-1033 | 629 |  |  | 298 |  |  | 927
PSS-1-26 | MF4-1512 | 713 |  |  | 345 |  |  | 1058
| MF4-1533 | 713 |  |  | 298 |  |  | 1011
PSS-1-31 | MF4-1512 | 841 |  |  | 345 |  |  | 1186
| MF4-1533 | 841 |  |  | 298 |  |  | 1139
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-1-13 | MF4-1012 | 3.6 |  |  | 10.9 |  |  | 14.5
| MF4-1033 |  |  |  | 10.9 |  |  | 14.5
PSS-1-18 | MF4-1012 | 4.4 |  |  | 10.9 |  |  | 15.3
| MF4-1033 |  |  |  | 10.9 |  |  | 15.3
PSS-1-22 | MF4-1012 | 5.1 |  |  | 10.9 |  |  | 16
| MF4-1033 |  |  |  | 10.9 |  |  | 16
PSS-1-26 | MF4-1512 | 5.8 |  |  | 12.6 |  |  | 18.4
| MF4-1533 |  |  |  | 11.5 |  |  | 17.3
PSS-1-31 | MF4-1512 | 8.8 |  |  | 12.6 |  |  | 21.4
| MF4-1533 |  |  |  | 11.5 |  |  | 20.3
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 1 1/4" (32mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-1 Series
98mm
P.L
M.L
T.L
Cable Guard Included
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Screw |  |  | - |  | 1
3 | Valve guide |  |  | - |  | 1
4 | Valve cone |  |  | STS304 |  | 1
5 | Valve seat |  |  | NBR |  | 1
6 | Valve casing |  |  | STS304 |  | 1
7 | Stop ring |  |  |  |  | 1
8 | Lock nut |  |  |  |  | 1
9 | Stop ring washer |  |  |  |  | 1
10 | Impeller |  |  |  |  | Stages
11 | Neck ring |  |  | NBR |  | Stages
12 | Bearing |  |  |  |  | Stages
13 | Diffuser |  |  | STS304 |  | Stages
14 | Spacer |  |  | - |  | 1
15 | Pump shaft/coupling |  |  | STS431/304 |  | 1
16 | Strainer |  |  | STS304 |  | 1
17 | Suction interconnector |  |  |  |  | 1
18 | Screw |  |  | - |  | 4
19 | Washer |  |  | STS304 |  | 4
20 | Strap |  |  |  |  | 4
21 | Cable GUARD |  |  |  |  | 1
22 | Check valve |  |  | - |  | 1
23 | Diffuseer Assy |  |  | - |  | Stages
24 | Strainer Assy |  |  | - |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-1 Series

## Test Report(1-22)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.1 | 15.4 | 19.6 | 25.2 | 30.3 | 35.1 | 40.1
Dis. Head | (m) | 183 | 167 | 145 | 120 | 76 | 41 | 19 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0022351 | 0.0051964 | 0.0084173 | 0.013914 | 0.020116 | 0.026994 | 0.035233
Total Head | (m) | 184 | 168.0022 | 146.0052 | 121.0084 | 77.0139 | 42.0201 | 20.027 | 1.5352
Water Power | (㎾) | 0 | 0.27658 | 0.3665 | 0.3866 | 0.31634 | 0.20753 | 0.11458 | 0.010035
Shaft Power | (㎾) | 0.58491 | 0.78982 | 0.88511 | 0.92988 | 0.93619 | 0.92471 | 0.9184 | 0.94193
Pump Eff. | (%) | 0 | 35.0182 | 41.4076 | 41.575 | 33.7903 | 22.443 | 12.4761 | 1.0653
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.11 | 8.22 | 8.84 | 9.13 | 9.18 | 9.13 | 9.05 | 9.21
Motor Input | (㎾) | 1.019 | 1.376 | 1.542 | 1.62 | 1.631 | 1.611 | 1.6 | 1.641
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 20 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 28
Item No. |  |  |  |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-1-22_MF4-1012 |  | Customer |  |  |  | 2 |  | 06/046/13
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification