## DataSheet(PSS-125-1-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-1-A_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 22 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 30 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 652 | mm | Pump | 43.3 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1363 | mm | Total | 101.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-125-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-1_MF6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 30 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 42 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 46 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 652 | mm | Pump | 60.3 | kg
37 | Motor | 841 | mm | Motor | 70 | kg
38 | Total | 1493 | mm | Total | 130.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-125-2-AA)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-2-AA_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 58 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 55.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 807 | mm | Pump | 67.2 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 1714 | mm | Total | 143.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-125-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-2_MF6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 63 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 83 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 74.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 807 | mm | Pump | 80 | kg
37 | Motor | 1036 | mm | Motor | 92 | kg
38 | Total | 1843 | mm | Total | 172 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-125-3-AA)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-3-AA_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 100 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 95 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 963 | mm | Pump | 100.4 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 2368 | mm | Total | 236.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-125-3-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-3-A_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 85 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 110 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 95 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 963 | mm | Pump | 100.4 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 2368 | mm | Total | 236.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-125-3)
Submersible Motor Pump Data Sheet
1 | Model | PSS-125-3_MF6-60033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 2000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 125 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1000 | ℓ/min | Coupling | STS304
15 | Max. Flow | 2600 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 45 | kW | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 111 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 963 | mm | Pump | 100.4 | kg
37 | Motor | 1560 | mm | Motor | 150 | kg
38 | Total | 2523 | mm | Total | 250.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-125-1-A | MF6-15033 | 652 |  |  | 711 |  |  | 1363
PSS-125-1 | MF6-25033 | 652 |  |  | 841 |  |  | 1493
PSS-125-2-AA | MF6-30033 | 807 |  |  | 907 |  |  | 1714
PSS-125-2 | MF6-40033 | 807 |  |  | 1036 |  |  | 1843
PSS-125-3-AA | MF6-50033 | 963 |  |  | 1405 |  |  | 2368
PSS-125-3-A | MF6-50033 | 963 |  |  | 1405 |  |  | 2368
PSS-125-3 | MF6-60033 | 963 |  |  | 1560 |  |  | 2523
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-125-1-A | MF6-15033 | 43.3 |  |  | 58 |  |  | 101.3
PSS-125-1 | MF6-25033 | 60.3 |  |  | 70 |  |  | 130.3
PSS-125-2-AA | MF6-30033 | 67.2 |  |  | 76 |  |  | 143.2
PSS-125-2 | MF6-40033 | 80 |  |  | 92 |  |  | 172
PSS-125-3-AA | MF6-50033 | 100.4 |  |  | 136 |  |  | 236.4
PSS-125-3-A | MF6-50033 | 100.4 |  |  | 136 |  |  | 236.4
PSS-125-3 | MF6-60033 | 100.4 |  |  | 150 |  |  | 250.4
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 6" (150mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-125 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  |  | MATERIAL | Q'TY
1 | Discharge |  |  |  | STS304 | 1
2 | Spring |  |  |  |  | 1
3 | Upper Retainer |  |  |  |  | 1
4 | Lower Retainer |  |  |  |  | 1
5 | O-ring |  |  |  | NBR | 1
6 | Diffuser |  |  |  | STS304 | Stages
7 | Neck Ring |  |  |  | STS304+NBR | Stages
8 | Split Cone Nut |  |  |  | STS304 | Stages
9 | Ring Of Impeller |  |  |  |  | Stages
10 | Impeller |  |  |  |  | Stages
11 | Space Washer |  |  |  | MoO2+PTFE | 1
12 | Nut for Stop Ring |  |  |  | STS304 | 1
13 | Shaft |  |  |  | STS431 | 1
14 | Screw |  |  |  | STS304 | 2
15 | Key |  |  |  |  | 2
16 | Strainer |  |  |  |  | 1
17 | Cable Guard |  |  |  |  | 1~2
18 | Valve Cup |  |  |  |  | 1
19 | Valve Seat |  |  |  |  | 1
20 | Bearing |  |  |  | NBR | Stages
21 | Spilt Cone |  |  |  | STS304 | Stages
22 | Bearing |  |  |  | NBR | 1
23 | Stop Ring |  |  |  | STS304 | 1
24 | Bottom diffuser |  |  |  |  | 1
25 | Stap |  |  |  |  | 4
26 | Coupling |  |  |  | STS304 | 1
27 | Spring Washer |  |  |  | STS304 | 4
28 | Nut |  |  |  |  | 4
29 | O-ring |  |  |  | NBR | 1
30 | Pump Base |  |  |  | STS304 | 1
| TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
| SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-125 Series

## PSS-125-1-A_MF6-15033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000
Dis. Head | (m) | 28.8 | 27.9 | 25.2 | 23.1 | 20 | 16 | 9
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.011346 | 0.045383 | 0.10211 | 0.18153 | 0.28364 | 0.40845
Total Head | (m) | 31.4 | 30.5113 | 27.8454 | 25.8021 | 22.7815 | 18.8836 | 12.0084
Water Power | (㎾) | 0 | 2.4867 | 4.5388 | 6.3086 | 7.4268 | 7.6951 | 5.8721
Shaft Power | (㎾) | 6.48 | 7.52 | 8.56 | 9.44 | 10.4 | 11.36 | 11.44
Pump Eff. | (%) | 0 | 33.0675 | 53.0233 | 66.8286 | 71.4113 | 67.7384 | 51.3298
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 17.7 | 19.3 | 20.9 | 22.3 | 24.5 | 25.7 | 25.9
Motor Input | (㎾) | 8.1 | 9.4 | 10.7 | 11.8 | 13 | 14.2 | 14.3
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 22 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-1-A_MF6-15033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PSS-125-1-MF6-25033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000
Dis. Head | (m) | 42.5 | 41.6 | 37.9 | 33.5 | 29 | 25 | 19.8
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.011346 | 0.045383 | 0.10211 | 0.18153 | 0.28364 | 0.40845
Total Head | (m) | 45.1 | 44.2113 | 40.5454 | 36.2021 | 31.7815 | 27.8836 | 22.8084
Water Power | (㎾) | 0 | 3.6032 | 6.6089 | 8.8514 | 10.3608 | 11.3626 | 11.1533
Shaft Power | (㎾) | 10.578 | 11.89 | 12.628 | 13.776 | 15.252 | 16.646 | 17.302
Pump Eff. | (%) | 0 | 30.3047 | 52.3353 | 64.2524 | 67.9306 | 68.2602 | 64.4627
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 27.8 | 29.5 | 30.7 | 32.6 | 35.2 | 37.4 | 38.7
Motor Input | (㎾) | 12.9 | 14.5 | 15.4 | 16.8 | 18.6 | 20.3 | 21.1
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 46 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-1-MF6-25033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PSS-125-2-AA_MF6-30033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 620 | 1070 | 1520 | 2000 | 2540 | 3000
Dis. Head | (m) | 58 | 57 | 53.4 | 49.5 | 44.1 | 34 | 22
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.017445 | 0.051959 | 0.10485 | 0.18153 | 0.29279 | 0.40845
Total Head | (m) | 60.6 | 59.6174 | 56.052 | 52.2049 | 46.8815 | 36.8928 | 25.0084
Water Power | (㎾) | 0 | 6.0249 | 9.776 | 12.9343 | 15.2834 | 15.2744 | 12.2291
Shaft Power | (㎾) | 12.1606 | 14.8912 | 16.8428 | 18.8272 | 20.746 | 21.8448 | 21.771
Pump Eff. | (%) | 0 | 40.4597 | 58.0427 | 68.6999 | 73.669 | 69.9222 | 56.1717
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 31.4 | 35.42 | 38.73 | 42.2 | 45.6 | 47.63 | 47.5
Motor Input | (㎾) | 14.83 | 18.16 | 20.54 | 22.96 | 25.3 | 26.64 | 26.55
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-2-AA_MF6-30033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PSS-125-2_MF6-40033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000
Dis. Head | (m) | 83.6 | 83.2 | 77 | 70 | 61.9 | 53.7 | 41.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.011346 | 0.045383 | 0.10211 | 0.18153 | 0.28364 | 0.40845
Total Head | (m) | 86.2 | 85.8113 | 79.6454 | 72.7021 | 64.6815 | 56.5836 | 44.2084
Water Power | (㎾) | 0 | 6.9936 | 12.9822 | 17.7757 | 21.0862 | 23.0578 | 21.6179
Shaft Power | (㎾) | 19.9588 | 22.6156 | 24.354 | 26.814 | 29.4298 | 31.406 | 32.964
Pump Eff. | (%) | 0 | 30.9239 | 53.3062 | 66.2925 | 71.6491 | 73.4186 | 65.5804
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 49.54 | 53.24 | 55.93 | 59.23 | 64.46 | 68.24 | 69.65
Motor Input | (㎾) | 24.34 | 27.58 | 29.7 | 32.7 | 35.89 | 38.3 | 40.2
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 63 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 74.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-2_MF6-40033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PSS-125-3-AA_MF6-50033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000
Dis. Head | (m) | 100 | 96 | 95 | 86 | 75 | 60 | 45
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.011346 | 0.045383 | 0.10211 | 0.18153 | 0.28364 | 0.40845
Total Head | (m) | 102.6 | 98.6113 | 97.6454 | 88.7021 | 77.7815 | 62.8836 | 48.0084
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 95 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-3-AA_MF6-50033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head X Specification

## PSS-125-3-A_MF6-50033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000
Dis. Head | (m) | 110 | 108 | 105 | 96 | 85 | 72 | 56
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.011346 | 0.045383 | 0.10211 | 0.18153 | 0.28364 | 0.40845
Total Head | (m) | 112.6 | 110.6113 | 107.6454 | 98.7021 | 87.7815 | 74.8836 | 59.0084
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 85 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 95 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-3-A_MF6-50033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head X Specification

## PSS-125-3_MF6-60033
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000
Dis. Head | (m) | 125 | 124 | 120 | 108 | 100 | 86 | 71
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.011346 | 0.045383 | 0.10211 | 0.18153 | 0.28364 | 0.40845
Total Head | (m) | 127.6 | 126.6113 | 122.6454 | 110.7021 | 102.7815 | 88.8836 | 74.0084
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 2000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 45 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 150 | 2.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 111 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | Franklin | Turbin | 8 | 10
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-125-3_MF6-60033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head X Specification