## Datasheet(14-3)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-3_MS4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 20 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 28 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | Kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 375 | mm | Pump | 3.7 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 715 | mm | Total | 15.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(14-8)
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-8_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 55 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 28 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 700 | mm | Pump | 7 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1255 | mm | Total | 30.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-14-3 | MS4-3033 | 3 |  |  | 3 |  | 3 | 380 | 60
PSS-14-8 | MS4-5533 | 8 |  |  | 5.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-14-3 | MS4-3033 | 375 |  |  | 340 |  |  | 715
PSS-14-8 | MS4-5533 | 700 |  |  | 555 |  |  | 1255
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-14-3 | MS4-3033 | 3.7 |  |  | 11.4 |  |  | 15.1
PSS-14-8 | MS4-5533 | 7 |  |  | 23.4 |  |  | 30.4
※DISCHARGE CONNECTION : 2"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-14 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Stop ring |  |  | - |  | 1
4 | Check Valve |  |  | STS304 |  | 1
6 | Split cone |  |  |  |  | Stages
7 | Impeller |  |  |  |  | Stages
8 | Split cone nut |  |  |  |  | Stages
9 | Neck ring |  |  | NBR |  | Stages
10 | Diffuser |  |  | STS304 |  | Stages
11 | Guide |  |  |  |  | 1
12 | Strainer |  |  |  |  | 1
13 | Suction interconnector |  |  |  |  | 1
14 | Pump shaft/coupling |  |  | STS431/304 |  | 1
15 | Strap |  |  | STS304 |  | 4
16 | Nut |  |  |  |  | 4
17 | Cable guard |  |  |  |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-14 Series

## Test Report(14-3)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 150 | 230 | 300 | 400 | 436
Dis. Head | (m) | 28.7 | 27.5 | 26 | 22.6 | 18.7 | 8.8 | 3.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.03676 | 0.082711 | 0.19446 | 0.33084 | 0.58816 | 0.6988
Total Head | (m) | 29.7 | 28.5368 | 27.0827 | 23.7945 | 20.0308 | 10.3882 | 5.1988
Water Power | (㎾) | 0 | 0.46515 | 0.66217 | 0.89205 | 0.97951 | 0.67731 | 0.36947
Shaft Power | (㎾) | 0.81696 | 1.0937 | 1.2669 | 1.4992 | 1.6369 | 1.705 | 1.6872
Pump Eff. | (%) | 0 | 42.5291 | 52.268 | 59.5004 | 59.84 | 39.7258 | 21.8983
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.89 | 3.27 | 3.55 | 3.95 | 4.19 | 4.33 | 4.29
Motor Input | (㎾) | 1.104 | 1.478 | 1.712 | 2.026 | 2.212 | 2.304 | 2.28
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 230 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 20 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin | 30
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-3＿MS4-2033 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(14-8)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.07 | 0.14 | 0.21 | 0.29 | 0.35 | 0.4 | 0.458
Dis. Head | (m) | 78 | 76.5 | 71 | 64 | 52.5 | 39.9 | 25 | 3.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.018013 | 0.07205 | 0.16211 | 0.30915 | 0.45031 | 0.58816 | 0.7711
Total Head | (m) | 79 | 77.518 | 72.0721 | 65.1621 | 53.8092 | 41.3503 | 26.5882 | 4.9711
Water Power | (kW) | 0 | 0.88448 | 1.6447 | 2.2305 | 2.5436 | 2.359 | 1.7335 | 0.37111
Shaft Power | (kW) | 2.1829 | 2.6704 | 3.2255 | 3.743 | 4.0902 | 4.1549 | 4.1079 | 3.9755
Pump Eff. | (%) | 0 | 33.1221 | 50.9896 | 59.5917 | 62.1861 | 56.7769 | 42.1998 | 9.335
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.69 | 7.45 | 8.4 | 9.3 | 9.94 | 10.06 | 9.98 | 9.69
Motor Input | (kW) | 2.835 | 3.468 | 4.189 | 4.861 | 5.312 | 5.396 | 5.335 | 5.163
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.23 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 4 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 55 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77 | M/T Maker | Sumoto | Turbin | 27 | 24
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-8＿MS4-5533 |  | Customer |  |  |  | 1 |  | 2013.09.4
Checked By |  |  |  |  | Approved By
Vacuum | mmhg
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치
440V일때의 전류치 | [8 empty] | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification