## Datasheet (17-1)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-1_MS4-1533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 15 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.8 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 343 | mm | Pump | 5 | kg
37 | Motor | 295 | mm | Motor | 10.9 | kg
38 | Total | 638 | mm | Total | 15.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-2_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 22 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 30 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.8 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 403 | mm | Pump | 6.4 | kg
37 | Motor | 375 | mm | Motor | 16.4 | kg
38 | Total | 778 | mm | Total | 22.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-3)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-3_MS4-4033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 45 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 8.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 464 | mm | Pump | 7.9 | kg
37 | Motor | 480 | mm | Motor | 18.3 | kg
38 | Total | 944 | mm | Total | 26.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-9)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-9_MS6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 130 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 19.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 827 | mm | Pump | 16.6 | kg
37 | Motor | 600 | mm | Motor | 42 | kg
38 | Total | 1427 | mm | Total | 58.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-13)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-13_MS6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 220 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 29.4 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1069 | mm | Pump | 22.4 | kg
37 | Motor | 700 | mm | Motor | 48 | kg
38 | Total | 1769 | mm | Total | 70.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-18)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-18_MS6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 180 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 270 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 38 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 18 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1371 | mm | Pump | 29.6 | kg
37 | Motor | 760 | mm | Motor | 54 | kg
38 | Total | 2131 | mm | Total | 83.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-22)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-22_MS6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 250 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 320 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 45.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 22 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1613 | mm | Pump | 35.4 | kg
37 | Motor | 830 | mm | Motor | 65 | kg
38 | Total | 2443 | mm | Total | 100.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-26)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-26_MS6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 310 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 390 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 54.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 26 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1855 | mm | Pump | 41.2 | kg
37 | Motor | 890 | mm | Motor | 70 | kg
38 | Total | 2745 | mm | Total | 111.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-17-1 | MS4-1533 | 343 |  |  | 295 |  |  | 638
PSS-17-2 | MS4-3033 | 403 |  |  | 375 |  |  | 778
PSS-17-3 | MS4-4033 | 464 |  |  | 480 |  |  | 944
PSS-17-7 | MS6-10033 | 706 |  |  | 600 |  |  | 1306
PSS-17-8 | MS6-10033 | 766 |  |  | 600 |  |  | 1366
PSS-17-9 | MS6-10033 | 827 |  |  | 600 |  |  | 1427
PSS-17-12 | MS6-15033 | 1008 |  |  | 700 |  |  | 1708
PSS-17-13 | MS6-15033 | 1069 |  |  | 700 |  |  | 1769
PSS-17-16 | MS6-20033 | 1250 |  |  | 760 |  |  | 2010
PSS-17-18 | MS6-20033 | 1371 |  |  | 760 |  |  | 2131
PSS-17-20 | MS6-25033 | 1492 |  |  | 830 |  |  | 2322
PSS-17-22 | MS6-25033 | 1613 |  |  | 830 |  |  | 2443
PSS-17-24 | MS6-30033 | 1734 |  |  | 890 |  |  | 2624
PSS-17-26 | MS6-30033 | 1855 |  |  | 890 |  |  | 2745
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-17-1 | MS4-1533 | 5 |  |  | 10.9 |  |  | 15.9
PSS-17-2 | MS4-3033 | 6.4 |  |  | 14.2 |  |  | 20.6
PSS-17-3 | MS4-4033 | 7.9 |  |  | 18.3 |  |  | 26.2
PSS-17-7 | MS6-10033 | 13.7 |  |  | 42 |  |  | 55.7
PSS-17-8 | MS6-10033 | 15.1 |  |  | 42 |  |  | 57.1
PSS-17-9 | MS6-10033 | 16.6 |  |  | 42 |  |  | 58.6
PSS-17-12 | MS6-15033 | 20.9 |  |  | 48 |  |  | 68.9
PSS-17-13 | MS6-15033 | 22.4 |  |  | 48 |  |  | 70.4
PSS-17-16 | MS6-20033 | 26.7 |  |  | 54 |  |  | 80.7
PSS-17-18 | MS6-20033 | 29.6 |  |  | 54 |  |  | 83.6
PSS-17-20 | MS6-25033 | 32.5 |  |  | 65 |  |  | 97.5
PSS-17-22 | MS6-25033 | 35.4 |  |  | 65 |  |  | 100.4
PSS-17-24 | MS6-30033 | 38.3 |  |  | 70 |  |  | 108.3
PSS-17-26 | MS6-30033 | 41.2 |  |  | 70 |  |  | 111.2
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 2 1/2" (65mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
P.L
M.L
Cable Guard Included
Outline Drawing
of PSS-17 Series
T.L
145mm

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304 |  | 1
2 | Valve cone |  |  | STS304 |  | 1
3 | Valve seat |  |  | STS304 |  | 1
4 | Spilt cone nut |  |  | STS304 |  | Stages
5 | Impeller |  |  | STS304
6 | Split cone |  |  | STS304
7 | Nock ring |  |  | NBR
8 | Diffuser |  |  | STS304
9 | Bearing |  |  | NBR
10 | Cunnecting piece |  |  | STS304 |  | 1
11 | Strainer |  |  | STS304 |  | 1
12 | Suction interconnector |  |  | STS304 |  | 1
13 | Pump shaft/coupling |  |  | STS431/304 |  | 1
14 | Coupling |  |  | STS304 |  | 1
15 | Strap |  |  | STS304 |  | 4
16 | Nut |  |  | STS304 |  | 4
17 | Cable Guard |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
1
1
2
1
3
1
4
1
5
1
6
1
7
1
8
1
9
1
10
11
1
12
1
13
1
14
1
15
1
16
1
17
1
Outline Drawing
of PSS-17 Series

## Test Report(17-1)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 150 | 300 | 370 | 420 | 460
Dis. Head | (m) | 15.8 | 14.3 | 10.3 | 8 | 5.8 | 3.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.028959 | 0.11584 | 0.1762 | 0.22704 | 0.27235
Total Head | (m) | 17.5 | 16.029 | 12.1158 | 9.8762 | 7.727 | 5.4723
Water Power | (㎾) | 0 | 0.39191 | 0.59246 | 0.59563 | 0.52899 | 0.41032
Shaft Power | (㎾) | 0.6264 | 0.7776 | 0.9072 | 0.9648 | 0.9936 | 1.008
Pump Eff. | (%) | 0 | 50.3997 | 65.3069 | 61.7365 | 53.2401 | 40.706
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.46 | 2.65 | 2.84 | 2.94 | 2.99 | 3
Motor Input | (㎾) | 0.87 | 1.08 | 1.26 | 1.34 | 1.38 | 1.4
Motor Eff. | (%) | 72 | 72 | 72 | 72 | 72 | 72
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 72 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-1＿MS4-1533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 200 | 300 | 360 | 400 | 450 | 500 | 530
Dis. Head | (m) | 31.3 | 28 | 24 | 20 | 17.5 | 13 | 8 | 4.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.051483 | 0.11584 | 0.16681 | 0.20593 | 0.26063 | 0.32177 | 0.36154
Total Head | (m) | 33 | 29.7515 | 25.8158 | 21.8668 | 19.4059 | 14.9606 | 10.0218 | 6.2615
Water Power | (㎾) | 0 | 0.9699 | 1.2624 | 1.2831 | 1.2653 | 1.0974 | 0.81677 | 0.54093
Shaft Power | (㎾) | 1.1925 | 1.6125 | 1.815 | 1.9275 | 1.98 | 2.025 | 2.025 | 2.01
Pump Eff. | (%) | 0 | 60.1487 | 69.5534 | 66.5704 | 63.9024 | 54.1907 | 40.3345 | 26.9122
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.67 | 5.16 | 5.45 | 5.61 | 5.67 | 5.76 | 5.74 | 5.73
Motor Input | (㎾) | 1.59 | 2.15 | 2.42 | 2.57 | 2.64 | 2.7 | 2.7 | 2.68
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 22 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-2_MS4-3033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-3)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 200 | 300 | 350 | 400 | 500 | 540
Dis. Head | (m) | 46 | 42 | 35.5 | 31.3 | 26.5 | 12.7 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.051483 | 0.11584 | 0.15767 | 0.20593 | 0.32177 | 0.37531
Total Head | (m) | 47.7 | 43.7515 | 37.3158 | 33.1577 | 28.4059 | 14.7218 | 7.0753
Water Power | (㎾) | 0 | 1.4263 | 1.8247 | 1.8916 | 1.8521 | 1.1998 | 0.62277
Shaft Power | (㎾) | 1.7252 | 2.3636 | 2.698 | 2.8196 | 2.8956 | 2.9336 | 2.8576
Pump Eff. | (%) | 0 | 60.3443 | 67.6332 | 67.0891 | 63.9614 | 40.8994 | 21.7934
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.42 | 6.42 | 6.98 | 7.2 | 7.36 | 7.41 | 7.29
Motor Input | (㎾) | 2.27 | 3.11 | 3.55 | 3.71 | 3.81 | 3.86 | 3.76
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 8.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-3_MS4-4033 |  | Customer |  |  |  | 2 | 0
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-9)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 107 | 206 | 304 | 308 | 406 | 565
Dis. Head | (m) | 134.5 | 132 | 125 | 107.5 | 106 | 77.5 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014736 | 0.054619 | 0.11895 | 0.1221 | 0.21216 | 0.41087
Total Head | (m) | 137 | 134.5147 | 127.5546 | 110.1189 | 108.6221 | 80.2122 | 2.9109
Water Power | (㎾) | 0 | 2.3461 | 4.283 | 5.4566 | 5.4533 | 5.3083 | 0.26808
Shaft Power | (㎾) | 5.144 | 5.96 | 6.984 | 7.848 | 7.88 | 8.432 | 7.664
Pump Eff. | (%) | 0 | 39.3636 | 61.3263 | 69.5287 | 69.2039 | 62.954 | 3.4979
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.44 | 14.72 | 16.45 | 18.01 | 18.06 | 19.11 | 17.72
Motor Input | (㎾) | 6.43 | 7.45 | 8.73 | 9.81 | 9.85 | 10.54 | 9.58
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | SUMOTO | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-9_MS6-10033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-13)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 101 | 208 | 302 | 330 | 402 | 540
Dis. Head | (m) | 229 | 209 | 196 | 160 | 150 | 102 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01313 | 0.055684 | 0.11739 | 0.14016 | 0.208 | 0.37531
Total Head | (m) | 231.5 | 211.5131 | 198.5557 | 162.6174 | 152.6402 | 104.708 | 3.8753
Water Power | (㎾) | 0 | 3.4821 | 6.7318 | 8.005 | 8.2105 | 6.8611 | 0.34111
Shaft Power | (㎾) | 7.5719 | 9.1449 | 11.2266 | 12.0771 | 12.069 | 11.7126 | 9.5013
Pump Eff. | (%) | 0 | 38.0774 | 59.9632 | 66.2825 | 68.0298 | 58.5788 | 3.5901
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 19.41 | 21.9 | 25.6 | 27.15 | 27.14 | 26.46 | 22.47
Motor Input | (㎾) | 9.348 | 11.29 | 13.86 | 14.91 | 14.9 | 14.46 | 11.73
Motor Eff. | (%) | 81 | 81 | 81 | 81 | 81 | 81 | 81
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 150 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 29.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81 | Maker | SUMOTO | Turbin | 24 | 24
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-13_MS6-15033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-18)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 135 | 260 | 320 | 390 | 420 | 490
Dis. Head | (m) | 280 | 270 | 220 | 200 | 142 | 92 | 20
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023457 | 0.087007 | 0.1318 | 0.19576 | 0.22704 | 0.30903
Total Head | (m) | 281.5 | 271.5235 | 221.587 | 201.6318 | 143.6958 | 93.727 | 21.809
Water Power | (㎾) | 0 | 5.9749 | 9.3909 | 10.5171 | 9.1347 | 6.4166 | 1.7419
Shaft Power | (㎾) | 9.794 | 13.28 | 15.438 | 15.272 | 14.691 | 13.861 | 12.201
Pump Eff. | (%) | 0 | 44.9915 | 60.8295 | 68.8653 | 62.1792 | 46.2921 | 14.2766
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 25 | 30.2 | 33.7 | 33.6 | 32.5 | 31.1 | 28.6
Motor Input | (㎾) | 11.8 | 16 | 18.6 | 18.4 | 17.7 | 16.7 | 14.7
Motor Eff. | (%) | 83 | 83 | 83 | 83 | 83 | 83 | 83
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 180 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 38 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 83 | Maker | SUMOTO | Turbin | 19.5 | 19.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-18_MS6-20033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-22)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 214 | 320 | 420 | 519 | 563
Dis. Head | (m) | 335 | 334 | 312 | 257 | 183 | 75 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.058943 | 0.1318 | 0.22704 | 0.34669 | 0.40796
Total Head | (m) | 338 | 337.0129 | 315.0589 | 260.1318 | 186.227 | 78.3467 | 4.408
Water Power | (㎾) | 0 | 5.4933 | 10.9899 | 13.5685 | 12.7491 | 6.6279 | 0.40451
Shaft Power | (㎾) | 13.776 | 15.624 | 18.816 | 20.916 | 21.924 | 21.168 | 19.824
Pump Eff. | (%) | 0 | 35.1594 | 58.4071 | 64.8713 | 58.1514 | 31.3109 | 2.0405
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 32 | 34 | 40 | 42 | 43 | 42.8 | 41
Motor Input | (㎾) | 16.4 | 18.6 | 22.4 | 24.9 | 26.1 | 25.2 | 23.6
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 250 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 84 | Maker | SUMOTO | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-22_MS6-25033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-26)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 210 | 310 | 397 | 496 | 562
Dis. Head | (m) | 395 | 370 | 317 | 240 | 125 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.05676 | 0.12369 | 0.20286 | 0.31664 | 0.40652
Total Head | (m) | 397.5 | 372.5568 | 319.6237 | 242.7029 | 127.8166 | 3.9065
Water Power | (㎾) | 0 | 12.7526 | 16.1506 | 15.7055 | 10.3337 | 0.35786
Shaft Power | (㎾) | 15.385 | 21.42 | 23.8 | 25.5 | 24.82 | 23.035
Pump Eff. | (%) | 0 | 59.536 | 67.8596 | 61.5904 | 41.6346 | 1.5536
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 34 | 42 | 48 | 51 | 50 | 47
Motor Input | (㎾) | 18.1 | 25.2 | 28 | 30 | 29.2 | 27.1
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 310 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 54.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-22_MS6-25033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification