## Datasheet(3-5)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-5_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 45 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 272 | mm | Pump | 2.3 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 570 | mm | Total | 13.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-5_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 45 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 272 | mm | Pump | 2.3 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 570 | mm | Total | 13.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-7)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-7_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 48 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 64 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 45 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 314 | mm | Pump | 2.6 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 612 | mm | Total | 13.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-7)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-7_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 48 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 64 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 45 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 314 | mm | Pump | 2.6 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 612 | mm | Total | 13.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-9)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-9_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 62 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 82 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 654 | mm | Total | 13.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-9)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-7_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 62 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 82 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 654 | mm | Total | 13.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-13)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-13_MF4-1512 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 115 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 11.5 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 440 | mm | Pump | 3.8 | kg
37 | Motor | 345 | mm | Motor | 12.6 | kg
38 | Total | 785 | mm | Total | 16.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-13)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-13_MF4-1533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 115 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 3.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 440 | mm | Pump | 3.8 | kg
37 | Motor | 298 | mm | Motor | 11.5 | kg
38 | Total | 738 | mm | Total | 15.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-17)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-17_MF4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 155 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 524 | mm | Pump | 4.5 | kg
37 | Motor | 384 | mm | Motor | 14.5 | kg
38 | Total | 908 | mm | Total | 19 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-17)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-17_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 155 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 524 | mm | Pump | 4.5 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 870 | mm | Total | 17.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-23)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-23_MF4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 155 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 210 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 23 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 650 | mm | Pump | 5.7 | kg
37 | Motor | 560 | mm | Motor | 20 | kg
38 | Total | 1210 | mm | Total | 25.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-23)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-23_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 155 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 210 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 23 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 650 | mm | Pump | 5.7 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1150 | mm | Total | 22.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3-36)
Submersible Motor Pump Data Sheet
1 | Model | PSS-3-36_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 250 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | STS304
11 | Shut off Head | 330 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 85 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 36 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 946 | mm | Pump | 10.5 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1546 | mm | Total | 35.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-3-5 | MF4-1012 | 5 |  |  | 1 |  | 1 | 220 | 60
| MF4-1033 | [5 empty] | 3 | 380
PSS-3-7 | MF4-1012 | 7 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-3-9 | MF4-1012 | 9 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-3-13 | MF4-1512 | 13 |  |  | 1.5 |  | 1 | 220
| MF4-1533 | [5 empty] | 3 | 380
PSS-3-17 | MF4-2012 | 17 |  |  | 2 |  | 1 | 220
| MF4-2033 | [5 empty] | 3 | 380
PSS-3-23 | MF4-3012 | 23 |  |  | 3 |  | 1 | 220
| MF4-3033 | [5 empty] | 3 | 380
PSS-3-31 | MF4-5033 | 31 |  |  | 5 |  | 3 | 380
PSS-3-36 | MF4-5033 | 36 |  |  | 5 |  | 3 | 380
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-3-5 | MF4-1012 | 272 |  |  | 298 |  |  | 570
| MF4-1033 | 272 |  |  | 298 |  |  | 570
PSS-3-7 | MF4-1012 | 314 |  |  | 298 |  |  | 612
| MF4-1033 | 314 |  |  | 298 |  |  | 612
PSS-3-9 | MF4-1012 | 356 |  |  | 298 |  |  | 654
| MF4-1033 | 356 |  |  | 298 |  |  | 654
PSS-3-13 | MF4-1512 | 440 |  |  | 345 |  |  | 785
| MF4-1533 | 440 |  |  | 298 |  |  | 738
PSS-3-17 | MF4-2012 | 524 |  |  | 384 |  |  | 908
| MF4-2033 | 524 |  |  | 346 |  |  | 870
PSS-3-23 | MF4-3012 | 650 |  |  | 560 |  |  | 1210
| MF4-3033 | 650 |  |  | 500 |  |  | 1150
PSS-3-31 | MF4-5033 | 841 |  |  | 600 |  |  | 1441
PSS-3-36 | MF4-5033 | 946 |  |  | 600 |  |  | 1546
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-3-5 | MF4-1012 | 2.3 |  |  | 10.9 |  |  | 13.2
| MF4-1033 |  |  |  | 10.9 |  |  | 13.2
PSS-3-7 | MF4-1012 | 2.6 |  |  | 10.9 |  |  | 13.5
| MF4-1033 |  |  |  | 10.9 |  |  | 13.5
PSS-3-9 | MF4-1012 | 3 |  |  | 10.9 |  |  | 13.9
| MF4-1033 |  |  |  | 10.9 |  |  | 13.9
PSS-3-13 | MF4-1512 | 3.8 |  |  | 12.6 |  |  | 16.4
| MF4-1533 |  |  |  | 11.5 |  |  | 15.3
PSS-3-17 | MF4-2012 | 4.5 |  |  | 14.5 |  |  | 19
| MF4-2033 |  |  |  | 13.1 |  |  | 17.6
PSS-3-23 | MF4-3012 | 5.7 |  |  | 20 |  |  | 25.7
| MF4-3033 |  |  |  | 17 |  |  | 22.7
PSS-3-31 | MF4-5033 | 9.2 |  |  | 25 |  |  | 34.2
PSS-3-36 | MF4-5033 | 10.5 |  |  | 25 |  |  | 35.5
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 1 1/4" (32mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-3 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Screw |  |  | - |  | 1
3 | Valve guide |  |  | - |  | 1
4 | Valve cone |  |  | STS304 |  | 1
5 | Valve seat |  |  | NBR |  | 1
6 | Valve casing |  |  | STS304 |  | 1
7 | Stop ring |  |  |  |  | 1
8 | Lock nut |  |  |  |  | 1
9 | Stop ring washer |  |  |  |  | 1
10 | Impeller |  |  |  |  | Stages
11 | Neck ring |  |  | NBR |  | Stages
12 | Bearing |  |  |  |  | Stages
13 | Diffuser |  |  | STS304 |  | Stages
14 | Spacer |  |  | - |  | 1
15 | Pump shaft/coupling |  |  | STS431/304 |  | 1
16 | Strainer |  |  | STS304 |  | 1
17 | Suction interconnector |  |  |  |  | 1
18 | Screw |  |  | - |  | 4
19 | Washer |  |  | STS304 |  | 4
20 | Strap |  |  |  |  | 4
21 | Cable GUARD |  |  |  |  | 1
22 | Check valve |  |  | - |  | 1
23 | Diffuseer Assy |  |  | - |  | Stages
24 | Strainer Assy |  |  | - |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-3 Series

## Test Report(3-5)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 25 | 50 | 75 | 100 | 106
Dis. Head | (m) | 47 | 42.9 | 38 | 28.1 | 6.5 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013694 | 0.054777 | 0.12325 | 0.21911 | 0.24619
Total Head | (m) | 47.8 | 43.7137 | 38.8548 | 29.0232 | 7.5191 | 1.1462
Water Power | (㎾) | 0 | 0.17813 | 0.31667 | 0.35481 | 0.12256 | 0.019804
Shaft Power | (㎾) | 0.32201 | 0.43509 | 0.54013 | 0.60213 | 0.55735 | 0.53612
Pump Eff. | (%) | 0 | 40.9415 | 58.6274 | 58.9261 | 21.9899 | 3.694
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.22 | 6.58 | 6.92 | 7.18 | 6.98 | 6.87
Motor Input | (㎾) | 0.561 | 0.758 | 0.941 | 1.049 | 0.971 | 0.934
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.8
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | Franklin | Turbin | 31 | 31
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-5＿MF4-1012 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-5)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 25 | 50 | 75 | 100 | 106
Dis. Head | (m) | 47.2 | 42.9 | 38.1 | 28 | 6.6 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013694 | 0.054777 | 0.12325 | 0.21911 | 0.24619
Total Head | (m) | 48 | 43.7137 | 38.9548 | 28.9232 | 7.6191 | 1.1462
Water Power | (㎾) | 0 | 0.17813 | 0.31748 | 0.35359 | 0.12419 | 0.019804
Shaft Power | (㎾) | 0.3451 | 0.4767 | 0.5978 | 0.6615 | 0.6111 | 0.5866
Pump Eff. | (%) | 0 | 37.368 | 53.1083 | 53.4523 | 20.3226 | 3.376
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.83 | 1.94 | 2.08 | 2.16 | 2.11 | 2.05
Motor Input | (㎾) | 0.493 | 0.681 | 0.854 | 0.945 | 0.873 | 0.838
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | Franklin | Turbin | 30 | 29
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-5＿MF4-1033 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-7)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.9 | 60.7 | 71.6 | 80.7 | 105
Dis. Head | (m) | 65 | 60 | 52 | 45 | 37 | 30 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0089405 | 0.036653 | 0.08073 | 0.11233 | 0.14269 | 0.24157
Total Head | (m) | 66 | 61.0089 | 53.0367 | 46.0807 | 38.1123 | 31.1427 | 2.2416
Water Power | (㎾) | 0 | 0.20088 | 0.35358 | 0.45593 | 0.4448 | 0.40965 | 0.038364
Shaft Power | (㎾) | 0.43739 | 0.59237 | 0.77031 | 0.90061 | 0.9207 | 0.91036 | 0.8168
Pump Eff. | (%) | 0 | 33.911 | 45.901 | 50.6245 | 48.3114 | 44.9989 | 4.6969
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.49 | 7.13 | 8.13 | 8.97 | 9.09 | 9.02 | 8.4
Motor Input | (㎾) | 0.762 | 1.032 | 1.342 | 1.569 | 1.604 | 1.586 | 1.423
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 48 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 21
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-7_MF4-1012 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-7)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.9 | 60.7 | 71.6 | 80.7 | 105
Dis. Head | (m) | 65 | 60 | 52 | 45 | 37 | 30 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.003662 | 0.015013 | 0.033067 | 0.046009 | 0.058448 | 0.098946
Total Head | (m) | 65.5 | 60.5037 | 52.515 | 45.5331 | 37.546 | 30.5584 | 1.5989
Water Power | (㎾) | 0 | 0.19921 | 0.3501 | 0.45051 | 0.43819 | 0.40197 | 0.027366
Shaft Power | (㎾) | 0.43739 | 0.59237 | 0.77031 | 0.90061 | 0.9207 | 0.91036 | 0.8168
Pump Eff. | (%) | 0 | 33.6302 | 45.4496 | 50.0228 | 47.5936 | 44.1547 | 3.3504
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.762 | 1.032 | 1.342 | 1.569 | 1.604 | 1.586 | 1.423
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 48 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-7_MF4-1033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-9)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.9 | 60.7 | 71.6 | 80.7 | 105
Dis. Head | (m) | 83 | 77.5 | 70 | 60 | 50 | 39 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0089405 | 0.036653 | 0.08073 | 0.11233 | 0.14269 | 0.24157
Total Head | (m) | 84 | 78.5089 | 71.0367 | 61.0807 | 51.1123 | 40.1427 | 2.2416
Water Power | (㎾) | 0 | 0.2585 | 0.47358 | 0.60434 | 0.59652 | 0.52804 | 0.038364
Shaft Power | (㎾) | 0.43739 | 0.59237 | 0.77031 | 0.90061 | 0.9207 | 0.91036 | 0.8168
Pump Eff. | (%) | 0 | 43.6382 | 61.4793 | 67.1036 | 64.7903 | 58.0033 | 4.6969
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.49 | 7.13 | 8.13 | 8.97 | 9.09 | 9.02 | 8.4
Motor Input | (㎾) | 0.762 | 1.032 | 1.342 | 1.569 | 1.604 | 1.586 | 1.423
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 62 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 21
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-9_MF4-1012 |  | Customer |  |  |  | 2 |  | 06/04/12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-9)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.9 | 60.7 | 71.6 | 80.7 | 105
Dis. Head | (m) | 83 | 77.5 | 70 | 60 | 50 | 39 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.003662 | 0.015013 | 0.033067 | 0.046009 | 0.058448 | 0.098946
Total Head | (m) | 83.5 | 78.0037 | 70.515 | 60.5331 | 50.546 | 39.5584 | 1.5989
Water Power | (㎾) | 0 | 0.25683 | 0.4701 | 0.59892 | 0.58991 | 0.52036 | 0.027366
Shaft Power | (㎾) | 0.43739 | 0.59237 | 0.77031 | 0.90061 | 0.9207 | 0.91036 | 0.8168
Pump Eff. | (%) | 0 | 43.3573 | 61.0279 | 66.5019 | 64.0724 | 57.1591 | 3.3504
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.762 | 1.032 | 1.342 | 1.569 | 1.604 | 1.586 | 1.423
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-9_MF4-1033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-13)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.9 | 60.7 | 71.6 | 80.7 | 105
Dis. Head | (m) | 115 | 110 | 100 | 82 | 70 | 55 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0089405 | 0.036653 | 0.08073 | 0.11233 | 0.14269 | 0.24157
Total Head | (m) | 116 | 111.0089 | 101.0367 | 83.0807 | 71.1123 | 56.1427 | 2.2416
Water Power | (㎾) | 0 | 0.36551 | 0.67358 | 0.82201 | 0.82994 | 0.73851 | 0.038364
Shaft Power | (㎾) | 0.57912 | 0.78432 | 1.0199 | 1.1924 | 1.219 | 1.2054 | 1.0815
Pump Eff. | (%) | 0 | 46.6019 | 66.0425 | 68.935 | 68.0813 | 61.2686 | 3.5474
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.49 | 7.13 | 8.13 | 8.97 | 9.09 | 9.02 | 8.4
Motor Input | (㎾) | 0.762 | 1.032 | 1.342 | 1.569 | 1.604 | 1.586 | 1.423
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 90 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 11.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | FRANKLIN | Turbin | 21
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-13_MF4-1512 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-13)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.9 | 60.7 | 71.6 | 80.7 | 105
Dis. Head | (m) | 115 | 110 | 100 | 82 | 70 | 55 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.003662 | 0.015013 | 0.033067 | 0.046009 | 0.058448 | 0.098946
Total Head | (m) | 115.5 | 110.5037 | 100.515 | 82.5331 | 70.546 | 55.5584 | 1.5989
Water Power | (㎾) | 0 | 0.36384 | 0.6701 | 0.81659 | 0.82333 | 0.73082 | 0.027366
Shaft Power | (㎾) | 0.53048 | 0.97356 | 1.0488 | 1.1651 | 1.2624 | 1.2973 | 1.2107
Pump Eff. | (%) | 0 | 37.3726 | 63.8924 | 70.0888 | 65.2214 | 56.3332 | 2.2604
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.48 | 1.91 | 1.93 | 2.14 | 2.22 | 2.29 | 2.27
Motor Input | (㎾) | 0.698 | 1.281 | 1.38 | 1.533 | 1.661 | 1.707 | 1.593
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 90 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-13_MF4-1533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-17)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.4 | 65.5 | 80.2 | 102
Dis. Head | (m) | 157 | 143 | 129 | 100 | 68 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0089405 | 0.035762 | 0.094003 | 0.14093 | 0.22796
Total Head | (m) | 158 | 144.0089 | 130.0358 | 101.094 | 69.1409 | 3.228
Water Power | (㎾) | 0 | 0.47416 | 0.85631 | 1.0793 | 0.90385 | 0.053668
Shaft Power | (㎾) | 0.74304 | 1.0925 | 1.4916 | 1.8349 | 1.775 | 1.5934
Pump Eff. | (%) | 0 | 43.4 | 57.4095 | 58.8224 | 50.9201 | 3.3681
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.63 | 7.72 | 10.3 | 12.5 | 12.08 | 10.91
Motor Input | (㎾) | 1.08 | 1.588 | 2.168 | 2.667 | 2.58 | 2.316
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 187 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 49 | 33
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-17_MF4-2012 |  | Customer |  |  |  | 2 |  | 2006.09.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-17)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 40 | 60.1 | 66.5 | 80.1 | 101
Dis. Head | (m) | 158 | 143 | 130 | 110 | 100 | 70 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.035057 | 0.079142 | 0.096895 | 0.14058 | 0.22351
Total Head | (m) | 159 | 144.0088 | 131.0351 | 111.0791 | 101.0969 | 71.1406 | 3.2235
Water Power | (㎾) | 0 | 0.46947 | 0.85435 | 1.0882 | 1.0958 | 0.92883 | 0.053069
Shaft Power | (㎾) | 0.7104 | 1.0548 | 1.3844 | 1.6331 | 1.6567 | 1.6223 | 1.5098
Pump Eff. | (%) | 0 | 44.5074 | 61.7127 | 66.6318 | 66.1463 | 57.2534 | 3.515
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.92 | 3.35 | 3.89 | 4.37 | 4.42 | 4.36 | 4.13
Motor Input | (㎾) | 1.054 | 1.565 | 2.054 | 2.423 | 2.458 | 2.407 | 2.24
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin | 38 | 36
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-17_MF4-2033 |  | Customer |  |  |  | 2 |  | 06/09/05
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-23)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.5 | 40.3 | 60.5 | 67 | 80.4 | 102.7
Dis. Head | (m) | 216 | 197 | 180 | 152 | 140 | 100 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.009208 | 0.035585 | 0.080199 | 0.098358 | 0.14164 | 0.2311
Total Head | (m) | 217 | 198.0092 | 181.0356 | 153.0802 | 141.0984 | 101.1416 | 2.2311
Water Power | (㎾) | 0 | 0.66165 | 1.1892 | 1.5096 | 1.5409 | 1.3255 | 0.037349
Shaft Power | (㎾) | 1.0486 | 1.498 | 1.9775 | 2.3779 | 2.4255 | 2.3639 | 2.009
Pump Eff. | (%) | 0 | 44.1687 | 60.1368 | 63.4846 | 63.5306 | 56.0718 | 1.8591
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.72 | 10.24 | 13.32 | 15.92 | 16.24 | 15.82 | 13.43
Motor Input | (㎾) | 1.498 | 2.14 | 2.825 | 3.397 | 3.465 | 3.377 | 2.87
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 155 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 44 | 26
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-23_MF4-3012 |  | Customer |  |  |  | 2 |  | 2006.09.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-23)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.5 | 40.1 | 60.8 | 65 | 80.2 | 101.2
Dis. Head | (m) | 215 | 195 | 176 | 148 | 140 | 95 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.009208 | 0.035233 | 0.080997 | 0.092573 | 0.14093 | 0.2244
Total Head | (m) | 216 | 196.0092 | 177.0352 | 149.081 | 141.0926 | 96.1409 | 2.2244
Water Power | (㎾) | 0 | 0.65496 | 1.1572 | 1.4775 | 1.4949 | 1.2568 | 0.036693
Shaft Power | (㎾) | 0.99918 | 1.494 | 1.9683 | 2.3424 | 2.3702 | 2.3153 | 2.0101
Pump Eff. | (%) | 0 | 43.8393 | 58.7882 | 63.0743 | 63.0692 | 54.2825 | 1.8254
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.84 | 4.39 | 5.12 | 5.81 | 5.84 | 5.72 | 5.2
Motor Input | (㎾) | 1.365 | 2.041 | 2.689 | 3.2 | 3.238 | 3.163 | 2.746
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 155 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 40 | 30
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-23_MF4-3033 |  | Customer |  |  |  | 2 |  | 06/09/08
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3-36)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.2 | 60.3 | 67.8 | 80.2 | 98.7
Dis. Head | (m) | 335 | 305 | 275 | 230 | 200 | 135 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0089405 | 0.035409 | 0.07967 | 0.10072 | 0.14093 | 0.21345
Total Head | (m) | 336 | 306.0089 | 276.0354 | 231.0797 | 201.1007 | 136.1409 | 2.2134
Water Power | (㎾) | 0 | 1.0076 | 1.8087 | 2.2713 | 2.2224 | 1.7797 | 0.03561
Shaft Power | (㎾) | 1.7517 | 2.5708 | 3.3289 | 3.8546 | 3.887 | 3.7535 | 3.2764
Pump Eff. | (%) | 0 | 39.1933 | 54.3353 | 58.9234 | 57.1761 | 47.4153 | 1.0869
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.39 | 7.28 | 8.34 | 9.2 | 9.27 | 9.05 | 8.26
Motor Input | (㎾) | 2.269 | 3.33 | 4.312 | 4.993 | 5.035 | 4.862 | 4.244
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 250 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-3-36_MF4-5033 |  | Customer |  |  |  | 2 |  | 06/09/12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification