## Datasheet(30-1)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-1_MS4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 15 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 250 | ℓ/min | Coupling | STS304
15 | Max. Flow | 750 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 366 | mm | Pump | 6.7 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 706 | mm | Total | 18.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-2_MS4-4033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 23 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 30 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 250 | ℓ/min | Coupling | STS304
15 | Max. Flow | 750 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 8.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 462 | mm | Pump | 8.4 | kg
37 | Motor | 480 | mm | Motor | 18.3 | kg
38 | Total | 942 | mm | Total | 26.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-5)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-5_MS6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 60 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 80 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 250 | ℓ/min | Coupling | STS304
15 | Max. Flow | 750 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 19.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 750 | mm | Pump | 13.5 | kg
37 | Motor | 600 | mm | Motor | 42 | kg
38 | Total | 1350 | mm | Total | 55.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-8)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-8_MS6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 125 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 29.4 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1038 | mm | Pump | 18.6 | kg
37 | Motor | 700 | mm | Motor | 48 | kg
38 | Total | 1749 | mm | Total | 66.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-11)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-11_MS6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 178 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 38 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1326 | mm | Pump | 23.6 | kg
37 | Motor | 760 | mm | Motor | 54 | kg
38 | Total | 2086 | mm | Total | 77.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-14)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-14_MS6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 160 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 228 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 45.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1518 | mm | Pump | 28.7 | kg
37 | Motor | 830 | mm | Motor | 65 | kg
38 | Total | 2348 | mm | Total | 93.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-17)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-17_MS6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 285 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 54.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1902 | mm | Pump | 33.8 | kg
37 | Motor | 890 | mm | Motor | 70 | kg
38 | Total | 2792 | mm | Total | 103.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-30-1 | MS4-2033 | 366 |  |  | 375 |  |  | 741
PSS-30-2 | MS4-4033 | 462 |  |  | 480 |  |  | 942
PSS-30-5 | MS6-10033 | 750 |  |  | 600 |  |  | 1350
PSS-30-8 | MS6-15033 | 1038 |  |  | 700 |  |  | 1738
PSS-30-11 | MS6-20033 | 1326 |  |  | 760 |  |  | 2086
PSS-30-12 | MS6-25033 | 1422 |  |  | 830 |  |  | 2252
PSS-30-14 | MS6-25033 | 1518 |  |  | 830 |  |  | 2348
PSS-30-15 | MS6-30033 | 1710 |  |  | 890 |  |  | 2600
PSS-30-17 | MS6-30033 | 1902 |  |  | 890 |  |  | 2792
PSS-30-21 | MS6-40033 | 2286 |  |  | 1030 |  |  | 3316
PSS-30-23 | MS6-40033 | 2478 |  |  | 1030 |  |  | 3508
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-30-1 | MS4-2033 | 6.7 |  |  | 11.4 |  |  | 18.1
PSS-30-2 | MS4-4033 | 8.4 |  |  | 18.3 |  |  | 26.7
PSS-30-5 | MS6-10033 | 13.5 |  |  | 42 |  |  | 55.5
PSS-30-8 | MS6-15033 | 18.6 |  |  | 48 |  |  | 66.6
PSS-30-11 | MS6-20033 | 23.6 |  |  | 54 |  |  | 77.6
PSS-30-12 | MS6-25033 | 25.3 |  |  | 65 |  |  | 90.3
PSS-30-14 | MS6-25033 | 28.7 |  |  | 65 |  |  | 93.7
PSS-30-15 | MS6-30033 | 30.4 |  |  | 70 |  |  | 100.4
PSS-30-17 | MS6-30033 | 33.8 |  |  | 70 |  |  | 103.8
PSS-30-21 | MS6-40033 | 40.6 |  |  | 90 |  |  | 130.6
PSS-30-23 | MS6-40033 | 44 |  |  | 90 |  |  | 134
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 3" (80mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-30 Series
145mm

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304 |  | 1
2 | Valve Cone |  |  |  |  | 1
3 | Valve Seat |  |  | NBR |  | Stages
4 | Top Diffuser |  |  | STS304 |  | 1
5 | Upper Bearing |  |  |  |  | 1
6 | Neck Ring |  |  | NBR |  | 1
7 | Bearing |  |  |  |  | 1
8 | Diffuser |  |  | STS304 |  | Stages
9 | Split Cone Nut |  |  |  |  | Stages
10 | Split Cone |  |  |  |  | Stages
11 | Impeller Ring |  |  |  |  | Stages
12 | Impeller |  |  |  |  | Stages
13 | Buttom Diffuser |  |  |  |  | 1
14 | Lower Bearing |  |  | - |  | 1
15 | Stop Ring |  |  | - |  | 1
16 | Space Washer |  |  | STS304 |  | 1
17 | Nut for Stop Ring |  |  |  |  | 1
18 | Buttom Neck Ring |  |  | NBR |  | 1
19 | Strainer |  |  | STS304 |  | 1
20 | Suction Interconnector |  |  |  |  | 1
21 | Pump Shaft |  |  | STS431 |  | 1
22 | Coupling |  |  | STS304 |  | 1
23 | Strap |  |  | STS304 |  | 4
24 | Nut |  |  | STS304 |  | 4
25 | Cable GUARD |  |  | STS304 |  | 1
26 | Strainer Cap |  |  |  |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-30 Series

## Test Report(30-1)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 400 | 500 | 600 | 700 | 800
Dis. Head | (m) | 15.5 | 13.2 | 11.7 | 10 | 8.5 | 6.3 | 3.7
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.050483 | 0.089747 | 0.14023 | 0.20193 | 0.27485 | 0.35899
Total Head | (m) | 17.2 | 14.9505 | 13.4897 | 11.8402 | 10.4019 | 8.2748 | 5.759
Water Power | (㎾) | 0 | 0.73108 | 0.87953 | 0.96498 | 1.0173 | 0.94416 | 0.75097
Shaft Power | (㎾) | 1.0212 | 1.295 | 1.3542 | 1.4208 | 1.5022 | 1.5614 | 1.5762
Pump Eff. | (%) | 0 | 56.4539 | 64.9484 | 67.918 | 67.7213 | 60.4688 | 47.6445
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.15 | 3.6 | 3.71 | 3.81 | 3.96 | 4.07 | 4.1
Motor Input | (㎾) | 1.38 | 1.75 | 1.83 | 1.92 | 2.03 | 2.11 | 2.13
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-1_MS4-2033 |  | Customer |  |  |  | 2 |  | 2009.05.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(30-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 400 | 500 | 630 | 700 | 800 | 900
Dis. Head | (m) | 32 | 28.5 | 25.8 | 23 | 18.8 | 16 | 11.2 | 5.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.050483 | 0.089747 | 0.14023 | 0.22263 | 0.27485 | 0.35899 | 0.45434
Total Head | (m) | 33.7 | 30.2505 | 27.5897 | 24.8402 | 20.7226 | 17.9748 | 13.259 | 7.6543
Water Power | (㎾) | 0 | 1.4792 | 1.7989 | 2.0245 | 2.128 | 2.0509 | 1.729 | 1.1229
Shaft Power | (㎾) | 2.1868 | 2.7566 | 2.8798 | 2.9876 | 3.157 | 3.1955 | 3.1955 | 3.1185
Pump Eff. | (%) | 0 | 53.6621 | 62.4645 | 67.7627 | 67.406 | 64.1818 | 54.1065 | 36.0074
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.06 | 7.02 | 7.22 | 7.42 | 7.73 | 7.79 | 7.79 | 7.67
Motor Input | (㎾) | 2.84 | 3.58 | 3.74 | 3.88 | 4.1 | 4.15 | 4.15 | 4.05
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.0 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 23 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 8.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-2_MS4-4033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(30-5)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 374 | 514 | 624 | 696 | 776 | 842 | 934
Dis. Head | (m) | 83 | 70 | 60 | 50 | 40 | 30 | 20 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.078459 | 0.14819 | 0.21841 | 0.27172 | 0.33777 | 0.39767 | 0.48932
Total Head | (m) | 85.5 | 72.5785 | 62.6482 | 52.7184 | 42.7717 | 32.8378 | 22.8977 | 7.9893
Water Power | (㎾) | 0 | 4.4245 | 5.2488 | 5.3621 | 4.8524 | 4.1536 | 3.1426 | 1.2163
Shaft Power | (㎾) | 4.944 | 6.72 | 7.288 | 7.568 | 7.608 | 7.584 | 7.504 | 7.2
Pump Eff. | (%) | 0 | 65.8412 | 72.0196 | 70.8522 | 63.7798 | 54.7677 | 41.8792 | 16.8932
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.26 | 16.14 | 17.13 | 17.65 | 17.71 | 17.68 | 17.51 | 16.96
Motor Input | (㎾) | 6.18 | 8.4 | 9.11 | 9.46 | 9.51 | 9.48 | 9.38 | 9
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | SUMOTO | Turbin | 19 | 19
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-5_MS6-10033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(30-8)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 380 | 570 | 710 | 815 | 994
Dis. Head | (m) | 128 | 110 | 90 | 70 | 50 | 0
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0.080997 | 0.18224 | 0.28276 | 0.37258 | 0.55421
Total Head | (m) | 135.8 | 117.881 | 97.9822 | 78.0828 | 58.1726 | 8.3542
Water Power | (㎾) | 0 | 7.3015 | 9.1035 | 9.0365 | 7.7279 | 1.3536
Shaft Power | (㎾) | 8.0271 | 11.7288 | 12.1743 | 12.393 | 12.3525 | 10.7244
Pump Eff. | (%) | 0 | 62.2532 | 74.7766 | 72.9163 | 62.5617 | 12.6214
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 20.42 | 25.26 | 27.44 | 27.84 | 27.78 | 24.98
Motor Input | (㎾) | 9.91 | 14.48 | 15.03 | 15.3 | 15.25 | 13.24
Motor Eff. | (%) | 81 | 81 | 81 | 81 | 81 | 81
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 29.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81 | Maker | SUMOTO | Turbin | 19 | 19
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-8_MS6-15033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-11)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 348 | 550 | 688 | 835 | 904 | 985
Dis. Head | (m) | 180 | 160 | 130 | 100 | 60 | 40 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.067929 | 0.16968 | 0.26551 | 0.39109 | 0.45839 | 0.54422
Total Head | (m) | 182.5 | 162.5679 | 132.6697 | 102.7655 | 62.8911 | 42.9584 | 8.0442
Water Power | (㎾) | 0 | 9.2215 | 11.8938 | 11.5245 | 8.5598 | 6.33 | 1.2915
Shaft Power | (㎾) | 10.9975 | 14.7325 | 16.517 | 16.849 | 16.6332 | 16.2431 | 15.0396
Pump Eff. | (%) | 0 | 62.5929 | 72.0097 | 68.3989 | 51.4621 | 38.9704 | 8.5876
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 26.27 | 32.56 | 35.88 | 36.48 | 36.05 | 35.37 | 33.16
Motor Input | (㎾) | 13.25 | 17.75 | 19.9 | 20.3 | 20.04 | 19.57 | 18.12
Motor Eff. | (%) | 83 | 83 | 83 | 83 | 83 | 83 | 83
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 38 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 83 | Maker | SUMOTO | Turbin | 15
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-11_MS6-20033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-14)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 270 | 480 | 570 | 650 | 775 | 920
Dis. Head | (m) | 230 | 210 | 170 | 150 | 120 | 80 | 9
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.040891 | 0.12924 | 0.18224 | 0.23699 | 0.3369 | 0.47476
Total Head | (m) | 231.5 | 211.5409 | 171.6292 | 151.6822 | 121.737 | 81.8369 | 10.9748
Water Power | (㎾) | 0 | 9.3099 | 13.4283 | 14.0928 | 12.898 | 10.338 | 1.6458
Shaft Power | (㎾) | 14.112 | 18.564 | 21.084 | 21.42 | 21.252 | 20.832 | 18.06
Pump Eff. | (%) | 0 | 50.1504 | 63.6894 | 65.7927 | 60.6909 | 49.6258 | 9.1128
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 33.6 | 40.4 | 42.5 | 42.9 | 42.7 | 41.9 | 39.5
Motor Input | (㎾) | 16.8 | 22.1 | 25.1 | 25.5 | 25.3 | 24.8 | 21.5
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 160 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 84 | Maker | SUMOTO | Turbin | 19.5 | 19.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-14_MS6-25033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-17)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 320 | 530 | 720 | 840 | 960
Dis. Head | (m) | 290 | 260 | 210 | 150 | 100 | 10
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.057438 | 0.15756 | 0.29078 | 0.39578 | 0.51694
Total Head | (m) | 291.8 | 261.8574 | 211.9576 | 152.0908 | 102.1958 | 12.3169
Water Power | (㎾) | 0 | 13.6585 | 18.311 | 17.8494 | 13.9926 | 1.9274
Shaft Power | (㎾) | 0 | 0 | 0 | 0 | 0 | 0
Pump Eff. | (%)
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 39.2 | 48.6 | 52.2 | 53.2 | 52.3 | 48.4
Motor Input | (㎾)
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 550 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 54.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 21 | 21
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-17_MS6-30033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification