## Datasheet(30-1)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-1_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 15 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 250 | ℓ/min | Coupling | STS304
15 | Max. Flow | 750 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 366 | mm | Pump | 6.7 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 712 | mm | Total | 19.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-2_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 23 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 30 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 250 | ℓ/min | Coupling | STS304
15 | Max. Flow | 750 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 462 | mm | Pump | 8.4 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1062 | mm | Total | 33.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-5)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-5_MF6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 60 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 80 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 250 | ℓ/min | Coupling | STS304
15 | Max. Flow | 750 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 750 | mm | Pump | 13.5 | kg
37 | Motor | 645 | mm | Motor | 52 | kg
38 | Total | 1395 | mm | Total | 65.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-8)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-8_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 125 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1038 | mm | Pump | 18.6 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1749 | mm | Total | 76.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-11)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-11_MF6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 178 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 37.3 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1326 | mm | Pump | 23.6 | kg
37 | Motor | 777 | mm | Motor | 64 | kg
38 | Total | 2103 | mm | Total | 87.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-14)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-14_MF6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 160 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 228 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 45.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1518 | mm | Pump | 28.7 | kg
37 | Motor | 841 | mm | Motor | 70 | kg
38 | Total | 2359 | mm | Total | 98.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-17)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-17_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 285 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 54.7 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1902 | mm | Pump | 33.8 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 2809 | mm | Total | 109.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-23)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-23_MF6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 270 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 360 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 75 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 23 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 2478 | mm | Pump | 44 | kg
37 | Motor | 1036 | mm | Motor | 92 | kg
38 | Total | 3514 | mm | Total | 136 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(30-28)
Submersible Motor Pump Data Sheet
1 | Model | PSS-30-28_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 340 | m | Discharge Piece | STS304
10 | Rated Capacity | 500 | ℓ/min | Impeller | STS304
11 | Shut off Head | 460 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 850 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 80 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 93.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 28 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 2958 | mm | Pump | 52.4 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 4363 | mm | Total | 188.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-30-1 | MF4-2012 | 366 |  |  | 384 |  |  | 750
| MF4-2033 |  |  |  | 346 |  |  | 712
PSS-30-2 | MF4-5033 | 462 |  |  | 600 |  |  | 1062
PSS-30-3-A | MF4-5033 | 558 |  |  | 600 |  |  | 1158
PSS-30-3 | MF4-5033 | 558 |  |  | 600 |  |  | 1158
PSS-30-4 | MF4-7533 | 654 |  |  | 752 |  |  | 1406
PSS-30-5 | MF6-10033 | 750 |  |  | 645 |  |  | 1395
PSS-30-8 | MF6-15033 | 1038 |  |  | 711 |  |  | 1749
PSS-30-11 | MF6-20033 | 1326 |  |  | 777 |  |  | 2103
PSS-30-12 | MF6-25033 | 1422 |  |  | 841 |  |  | 2263
PSS-30-14 | MF6-25033 | 1518 |  |  | 841 |  |  | 2359
PSS-30-15 | MF6-30033 | 1710 |  |  | 907 |  |  | 2617
PSS-30-17 | MF6-30033 | 1902 |  |  | 907 |  |  | 2809
PSS-30-21 | MF6-40033 | 2286 |  |  | 1036 |  |  | 3322
PSS-30-23 | MF6-40033 | 2478 |  |  | 1036 |  |  | 3514
PSS-30-24 | MF6-50033 | 2574 |  |  | 1405 |  |  | 3979
PSS-30-26 | MF6-50033 | 2766 |  |  | 1405 |  |  | 4171
PSS-30-28 | MF6-50033 | 2958 |  |  | 1405 |  |  | 4363
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-30-1 | MF4-2012 | 6.7 |  |  | 14.5 |  |  | 21.2
| MF4-2033 |  |  |  | 13.1 |  |  | 19.8
PSS-30-2 | MF4-5033 | 8.4 |  |  | 25 |  |  | 33.4
PSS-30-3-A | MF4-5033 | 10.1 |  |  | 25 |  |  | 35.1
PSS-30-3 | MF4-5033 | 10.1 |  |  | 25 |  |  | 35.1
PSS-30-4 | MF4-7533 | 11.8 |  |  | 31.8 |  |  | 43.6
PSS-30-5 | MF6-10033 | 13.5 |  |  | 52 |  |  | 65.5
PSS-30-8 | MF6-15033 | 18.6 |  |  | 58 |  |  | 76.6
PSS-30-11 | MF6-20033 | 23.6 |  |  | 64 |  |  | 87.6
PSS-30-12 | MF6-25033 | 25.3 |  |  | 70 |  |  | 95.3
PSS-30-14 | MF6-25033 | 28.7 |  |  | 70 |  |  | 98.7
PSS-30-15 | MF6-30033 | 30.4 |  |  | 76 |  |  | 106.4
PSS-30-17 | MF6-30033 | 33.8 |  |  | 76 |  |  | 109.8
PSS-30-21 | MF6-40033 | 40.6 |  |  | 92 |  |  | 132.6
PSS-30-23 | MF6-40033 | 44 |  |  | 92 |  |  | 136
PSS-30-24 | MF6-50033 | 45.6 |  |  | 136 |  |  | 181.6
PSS-30-26 | MF6-50033 | 49 |  |  | 136 |  |  | 185
PSS-30-28 | MF6-50033 | 52.4 |  |  | 136 |  |  | 188.4
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 3" (80mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
145mm
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-30 Series

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304 |  | 1
2 | Valve Cone |  |  |  |  | 1
3 | Valve Seat |  |  | NBR |  | Stages
4 | Top Diffuser |  |  | STS304 |  | 1
5 | Upper Bearing |  |  |  |  | 1
6 | Neck Ring |  |  | NBR |  | 1
7 | Bearing |  |  |  |  | 1
8 | Diffuser |  |  | STS304 |  | Stages
9 | Split Cone Nut |  |  |  |  | Stages
10 | Split Cone |  |  |  |  | Stages
11 | Impeller Ring |  |  |  |  | Stages
12 | Impeller |  |  |  |  | Stages
13 | Buttom Diffuser |  |  |  |  | 1
14 | Lower Bearing |  |  | - |  | 1
15 | Stop Ring |  |  | - |  | 1
16 | Space Washer |  |  | STS304 |  | 1
17 | Nut for Stop Ring |  |  |  |  | 1
18 | Buttom Neck Ring |  |  | NBR |  | 1
19 | Strainer |  |  | STS304 |  | 1
20 | Suction Interconnector |  |  |  |  | 1
21 | Pump Shaft |  |  | STS431 |  | 1
22 | Coupling |  |  | STS304 |  | 1
23 | Strap |  |  | STS304 |  | 4
24 | Nut |  |  | STS304 |  | 4
25 | Cable GUARD |  |  | STS304 |  | 1
26 | Strainer Cap |  |  |  |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-30 Series

## Test Report(30-1)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 200 | 400 | 648 | 750 | 917
Dis. Head | (m) | 15.7 | 15 | 12.7 | 8 | 6 | 0.9
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.022437 | 0.089747 | 0.23553 | 0.31552 | 0.47167
Total Head | (m) | 16.2 | 15.5224 | 13.2897 | 8.7355 | 6.8155 | 1.8717
Water Power | (㎾) | 0 | 0.50603 | 0.86649 | 0.92268 | 0.8332 | 0.27976
Shaft Power | (㎾) | 0.93147 | 1.0892 | 1.2267 | 1.4114 | 1.4464 | 1.4188
Pump Eff. | (%) | 0 | 46.4597 | 70.6371 | 65.3756 | 57.6047 | 19.7185
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.1 | 3.33 | 3.57 | 3.9 | 3.98 | 3.91
Motor Input | (㎾) | 1.382 | 1.616 | 1.82 | 2.094 | 2.146 | 2.105
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-1_MF4-2033 |  | Customer |  |  |  | 2 |  | 2009.05.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(30-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 202 | 400 | 523 | 600 | 802 | 973
Dis. Head | (m) | 32.8 | 31 | 27 | 23 | 21 | 11.3 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.022888 | 0.089747 | 0.15343 | 0.20193 | 0.36078 | 0.53104
Total Head | (m) | 33.3 | 31.5229 | 27.5897 | 23.6534 | 21.7019 | 12.1608 | 2.031
Water Power | (㎾) | 0 | 1.0379 | 1.7989 | 2.0164 | 2.1224 | 1.5897 | 0.32212
Shaft Power | (㎾) | 2.1577 | 2.4982 | 2.7738 | 2.9707 | 3.0756 | 3.1351 | 2.9483
Pump Eff. | (%) | 0 | 41.547 | 64.8516 | 67.8783 | 69.0082 | 50.7076 | 10.9258
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.14 | 7.5 | 7.91 | 8.2 | 8.37 | 8.43 | 8.19
Motor Input | (㎾) | 2.795 | 3.236 | 3.593 | 3.848 | 3.984 | 4.061 | 3.819
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 23 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-2_MF4-5033 |  | Customer |  |  |  | 2 |  | 2009.05.12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(30-5)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 374 | 514 | 624 | 696 | 776 | 842 | 934
Dis. Head | (m) | 83 | 70 | 60 | 50 | 40 | 30 | 20 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.078459 | 0.14819 | 0.21841 | 0.27172 | 0.33777 | 0.39767 | 0.48932
Total Head | (m) | 85.5 | 72.5785 | 62.6482 | 52.7184 | 42.7717 | 32.8378 | 22.8977 | 7.9893
Water Power | (㎾) | 0 | 4.4245 | 5.2488 | 5.3621 | 4.8524 | 4.1536 | 3.1426 | 1.2163
Shaft Power | (㎾) | 4.8204 | 6.552 | 7.1058 | 7.3788 | 7.4178 | 7.3944 | 7.3164 | 7.02
Pump Eff. | (%) | 0 | 67.5294 | 73.8663 | 72.6689 | 65.4152 | 56.172 | 42.953 | 17.3264
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.26 | 16.14 | 17.13 | 17.65 | 17.71 | 17.68 | 17.51 | 16.96
Motor Input | (㎾) | 6.18 | 8.4 | 9.11 | 9.46 | 9.51 | 9.48 | 9.38 | 9
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | Franklin | Turbin | 19 | 19
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-5_MF6-10033 |  | Customer |  |  |  | 2 |  | 2005.11.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(30-8)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 380 | 570 | 710 | 815 | 994
Dis. Head | (m) | 128 | 110 | 90 | 70 | 50 | 0
Suc. Head | (m) | 6 | 6 | 6 | 6 | 6 | 6
Speed Head | (m) | 0 | 0.080997 | 0.18224 | 0.28276 | 0.37258 | 0.55421
Total Head | (m) | 135.8 | 117.881 | 97.9822 | 78.0828 | 58.1726 | 8.3542
Water Power | (㎾) | 0 | 7.3015 | 9.1035 | 9.0365 | 7.7279 | 1.3536
Shaft Power | (㎾) | 7.9478 | 11.613 | 12.0541 | 12.2706 | 12.2305 | 10.6185
Pump Eff. | (%) | 0 | 62.8741 | 75.5225 | 73.6436 | 63.1858 | 12.7473
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 20.42 | 25.26 | 27.44 | 27.84 | 27.78 | 24.98
Motor Input | (㎾) | 9.91 | 14.48 | 15.03 | 15.3 | 15.25 | 13.24
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | Franklin | Turbin | 19 | 19
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-8_MF6-15033 |  | Customer |  |  |  | 2 |  | 2005.10.31
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-11)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 348 | 550 | 688 | 835 | 904 | 985
Dis. Head | (m) | 180 | 160 | 130 | 100 | 60 | 40 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.067929 | 0.16968 | 0.26551 | 0.39109 | 0.45839 | 0.54422
Total Head | (m) | 182.5 | 162.5679 | 132.6697 | 102.7655 | 62.8911 | 42.9584 | 8.0442
Water Power | (㎾) | 0 | 9.2215 | 11.8938 | 11.5245 | 8.5598 | 6.33 | 1.2915
Shaft Power | (㎾) | 10.812 | 14.484 | 16.2384 | 16.5648 | 16.3526 | 15.9691 | 14.7859
Pump Eff. | (%) | 0 | 63.6668 | 73.2451 | 69.5724 | 52.345 | 39.639 | 8.7349
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 26.27 | 32.56 | 35.88 | 36.48 | 36.05 | 35.37 | 33.16
Motor Input | (㎾) | 13.25 | 17.75 | 19.9 | 20.3 | 20.04 | 19.57 | 18.12
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 37.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | Franklin | Turbin | 15
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-11_MF6-20033 |  | Customer |  |  |  | 2 |  | 2005.11.22
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-14)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 270 | 480 | 570 | 650 | 775 | 920
Dis. Head | (m) | 230 | 210 | 170 | 150 | 120 | 80 | 9
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.040891 | 0.12924 | 0.18224 | 0.23699 | 0.3369 | 0.47476
Total Head | (m) | 231.5 | 211.5409 | 171.6292 | 151.6822 | 121.737 | 81.8369 | 10.9748
Water Power | (㎾) | 0 | 9.3099 | 13.4283 | 14.0928 | 12.898 | 10.338 | 1.6458
Shaft Power | (㎾) | 13.776 | 18.122 | 20.582 | 20.91 | 20.746 | 20.336 | 17.63
Pump Eff. | (%) | 0 | 51.3735 | 65.2428 | 67.3974 | 62.1712 | 50.8362 | 9.3351
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 33.6 | 40.4 | 44.5 | 44.9 | 44.7 | 43.9 | 39.5
Motor Input | (㎾) | 16.8 | 22.1 | 25.1 | 25.5 | 25.3 | 24.8 | 21.5
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 160 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 46 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | FRANKLIN | Turbin | 19.5 | 19.5
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-14_MF6-25033 |  | Customer |  |  |  | 2 |  | 06/09/22
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-17)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 320 | 530 | 720 | 840 | 960
Dis. Head | (m) | 290 | 260 | 210 | 150 | 100 | 10
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.057438 | 0.15756 | 0.29078 | 0.39578 | 0.51694
Total Head | (m) | 291.8 | 261.8574 | 211.9576 | 152.0908 | 102.1958 | 12.3169
Water Power | (㎾) | 0 | 13.6585 | 18.311 | 17.8494 | 13.9926 | 1.9274
Shaft Power | (㎾) | 0 | 0 | 0 | 0 | 0 | 0
Pump Eff. | (%)
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 39.2 | 48.6 | 54.2 | 55.2 | 54.3 | 48.4
Motor Input | (㎾)
Motor Eff. | (%) | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 550 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.6 | Maker | FRANKLIN | Turbin | 21 | 21
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-17_MF6-30033 |  | Customer |  |  |  | 3 |  | 2005.10.13
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-23)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 313 | 560 | 613 | 903 | 971
Dis. Head | (m) | 362 | 328 | 259 | 233 | 77 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.054953 | 0.1759 | 0.21078 | 0.45738 | 0.52886
Total Head | (m) | 365 | 331.055 | 262.1759 | 236.2108 | 80.4574 | 4.5289
Water Power | (㎾) | 0 | 16.8901 | 23.9314 | 23.6019 | 11.8424 | 0.7168
Shaft Power | (㎾) | 23.3496 | 29.6424 | 33.534 | 34.1136 | 32.7888 | 29.9736
Pump Eff. | (%) | 0 | 56.9795 | 71.3646 | 69.1863 | 36.1173 | 2.3914
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 54 | 65 | 72 | 73 | 70 | 65
Motor Input | (㎾) | 28.2 | 35.8 | 40.5 | 41.2 | 39.6 | 36.2
Motor Eff. | (%) | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 29 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 270 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.8 | Maker | FRANKLIN | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-23_MF6-40033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## TestReport(30-28)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 340 | 500 | 690 | 825 | 960
Dis. Head | (m) | 465 | 402 | 345 | 245 | 145 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.064842 | 0.14023 | 0.26705 | 0.38177 | 0.51694
Total Head | (m) | 466.8 | 403.8648 | 346.9402 | 247.0671 | 147.1818 | 7.3169
Water Power | (㎾) | 0 | 22.3822 | 28.2756 | 27.7876 | 19.7923 | 1.145
Shaft Power | (㎾) | 32.7031 | 39.0878 | 40.3218 | 40.7332 | 38.685 | 32.2489
Pump Eff. | (%) | 0 | 57.2614 | 70.1248 | 68.2186 | 51.1627 | 3.5504
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 79 | 80.2 | 88 | 90 | 87.6 | 79.1
Motor Input | (㎾) | 38.16 | 45.61 | 47.05 | 47.53 | 45.14 | 37.63
Motor Eff. | (%) | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 500 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 340 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 95 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85.7 | Maker | FRANKLIN | Turbin | 21 | 21
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-30-28_MF6-50033 |  | Customer |  |  |  | 2 |  | 2005.10.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification