## Datasheet(46-1-B)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1-B_MS4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 9 | m | Discharge Piece | STS304
10 | Rated Capacity | 600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 13 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 723 | mm | Total | 18.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-1-A)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1-A_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 17 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 758 | mm | Total | 21.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1_MS4-4033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 12 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 18 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 8.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 480 | mm | Motor | 18.3 | kg
38 | Total | 863 | mm | Total | 25.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-2-AB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-2-AB_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 20 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 33 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1051 | mm | Total | 32.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-2_MS4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 38 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1171 | mm | Total | 38.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-3-BB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-3-BB_MS4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 30 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 50 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 609 | mm | Pump | 11.5 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1284 | mm | Total | 40.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-3)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-3_MS6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 58 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 19.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 609 | mm | Pump | 11.5 | kg
37 | Motor | 600 | mm | Motor | 42 | kg
38 | Total | 1209 | mm | Total | 53.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-5-C)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-5-C_MS6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 65 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 90 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 29.4 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 835 | mm | Pump | 16 | kg
37 | Motor | 700 | mm | Motor | 48 | kg
38 | Total | 1535 | mm | Total | 64 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-10)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-10_MS6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 195 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 54.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1400 | mm | Pump | 27.4 | kg
37 | Motor | 890 | mm | Motor | 70 | kg
38 | Total | 2290 | mm | Total | 97.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-13)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-13_MS6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 225 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 75 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 2040 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | OIL Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1739 | mm | Pump | 34.3 | kg
37 | Motor | 1030 | mm | Motor | 90 | kg
38 | Total | 2769 | mm | Total | 124.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
| MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
| PSS-46-1-B | MS4-2033 | 383 |  |  | 340 |  |  | 723
| PSS-46-1-A | MS4-3033 | 383 |  |  | 375 |  |  | 758
| PSS-46-1 | MS4-4033 | 383 |  |  | 480 |  |  | 863
| PSS-46-2 | MS4-7533 | 496 |  |  | 675 |  |  | 1171
| PSS-46-3-BB | MS4-7533 | 609 |  |  | 675 |  |  | 1284
| PSS-46-3 | MS6-10033 | 609 |  |  | 600 |  |  | 1209
| PSS-46-4-BC | MS6-10033 | 722 |  |  | 600 |  |  | 1322
| PSS-46-5-C | MS6-15033 | 835 |  |  | 700 |  |  | 1535
| PSS-46-6 | MS6-20033 | 948 |  |  | 760 |  |  | 1708
| PSS-46-7-C | MS6-20033 | 1061 |  |  | 760 |  |  | 1821
| PSS-46-7 | MS6-25033 | 1061 |  |  | 830 |  |  | 1891
| PSS-46-8 | MS6-25033 | 1174 |  |  | 830 |  |  | 2004
| PSS-46-9 | MS6-30033 | 1287 |  |  | 890 |  |  | 2177
| PSS-46-10 | MS6-30033 | 1400 |  |  | 890 |  |  | 2290
| PSS-46-13 | MS6-40033 | 1739 |  |  | 1030 |  |  | 2769
123 | WEIGHT(kg)
| MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
| PSS-46-1-B | MS4-2033 | 6.9 |  |  | 11.4 |  |  | 18.3
| PSS-46-1-A | MS4-3033 | 6.9 |  |  | 14.2 |  |  | 21.1
| PSS-46-1 | MS4-4033 | 6.9 |  |  | 18.3 |  |  | 25.2
| PSS-46-2 | MS4-7533 | 9.2 |  |  | 29.4 |  |  | 38.6
| PSS-46-3-BB | MS4-7533 | 11.5 |  |  | 29.4 |  |  | 40.9
| PSS-46-3 | MS6-10033 | 11.5 |  |  | 42 |  |  | 53.5
| PSS-46-4-BC | MS6-10033 | 13.7 |  |  | 42 |  |  | 55.7
| PSS-46-5-C | MS6-15033 | 16 |  |  | 48 |  |  | 64
| PSS-46-6 | MS6-20033 | 18.3 |  |  | 54 |  |  | 72.3
| PSS-46-7-C | MS6-20033 | 20.6 |  |  | 54 |  |  | 74.6
| PSS-46-7 | MS6-25033 | 20.6 |  |  | 65 |  |  | 85.6
| PSS-46-8 | MS6-25033 | 22.9 |  |  | 65 |  |  | 87.9
| PSS-46-9 | MS6-30033 | 25.1 |  |  | 70 |  |  | 95.1
| PSS-46-10 | MS6-30033 | 27.4 |  |  | 70 |  |  | 97.4
| PSS-46-13 | MS6-40033 | 34.3 |  |  | 90 |  |  | 124.3
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 4" (100mm)
|  |  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
145mm
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-46 Series

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | 품 명 |  |  | 재 질 |  | 수량
1 | Discharge |  |  | STS304 |  | 1
2 | Valve Cone |  |  |  |  | 1
3 | Valve Seat |  |  | NBR |  | Stages
4 | Top Diffuser |  |  | STS304 |  | 1
5 | Upper Bearing |  |  |  |  | 1
6 | Neck Ring |  |  | NBR |  | 1
7 | Bearing |  |  |  |  | 1
8 | Diffuser |  |  | STS304 |  | Stages
9 | Split Cone Nut |  |  |  |  | Stages
10 | Split Cone |  |  |  |  | Stages
11 | Impeller Ring |  |  |  |  | Stages
12 | Impeller |  |  |  |  | Stages
13 | Buttom Diffuser |  |  |  |  | 1
14 | Lower Bearing |  |  | - |  | 1
15 | Stop Ring |  |  | - |  | 1
16 | Space Washer |  |  | STS304 |  | 1
17 | Nut for Stop Ring |  |  |  |  | 1
18 | Buttom Neck Ring |  |  | NBR |  | 1
19 | Strainer |  |  | STS304 |  | 1
20 | Suction Interconnector |  |  |  |  | 1
21 | Pump Shaft |  |  | STS431 |  | 1
22 | Coupling |  |  | STS304 |  | 1
23 | Strap |  |  |  |  | 4
24 | Nut |  |  |  |  | 4
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-46 Series

## Test Report(46-1-B)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 450 | 600 | 700 | 800 | 900 | 1000
Dis. Head | (m) | 13.8 | 12 | 10.4 | 8.5 | 7.4 | 6 | 4 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.046525 | 0.082711 | 0.11258 | 0.14704 | 0.1861 | 0.22975
Total Head | (m) | 15.5 | 13.7207 | 12.1465 | 10.2827 | 9.2126 | 7.847 | 5.8861 | 3.9298
Water Power | (㎾) | 0 | 0.67094 | 0.89095 | 1.0056 | 1.0512 | 1.0233 | 0.86349 | 0.64055
Shaft Power | (㎾) | 1.2802 | 1.3986 | 1.517 | 1.6354 | 1.702 | 1.7168 | 1.7094 | 1.665
Pump Eff. | (%) | 0 | 47.9723 | 58.7309 | 61.4925 | 61.76 | 59.6024 | 50.5143 | 38.4714
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.56 | 3.76 | 3.97 | 4.19 | 4.32 | 4.35 | 4.32 | 4.25
Motor Input | (㎾) | 1.73 | 1.89 | 2.05 | 2.21 | 2.3 | 2.32 | 2.31 | 2.25
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 9 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1-B_MS4-2033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-1-A)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 800 | 1000 | 1100
Dis. Head | (m) | 17.8 | 16 | 14 | 11.8 | 10.5 | 7.5 | 5.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.14704 | 0.22975 | 0.278
Total Head | (m) | 19.5 | 17.7207 | 15.7574 | 13.5971 | 12.347 | 9.4298 | 7.278
Water Power | (㎾) | 0 | 0.86654 | 1.2842 | 1.4406 | 1.6101 | 1.537 | 1.3049
Shaft Power | (㎾) | 1.7175 | 1.9125 | 2.0775 | 2.2275 | 2.3925 | 2.5125 | 2.52
Pump Eff. | (%) | 0 | 45.3093 | 61.8162 | 64.6738 | 67.2959 | 61.1761 | 51.7835
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.36 | 5.67 | 5.92 | 6.15 | 6.42 | 6.61 | 6.62
Motor Input | (㎾) | 2.29 | 2.55 | 2.77 | 2.97 | 3.19 | 3.35 | 3.36
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1-A_MS4-3033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 800 | 1000 | 1200
Dis. Head | (m) | 19.5 | 17.8 | 15.2 | 13.2 | 11.8 | 9 | 4.8
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.14704 | 0.22975 | 0.33084
Total Head | (m) | 21.2 | 19.5207 | 16.9574 | 14.9971 | 13.647 | 10.9298 | 6.8308
Water Power | (㎾) | 0 | 0.95456 | 1.382 | 1.5889 | 1.7796 | 1.7815 | 1.3361
Shaft Power | (㎾) | 1.9228 | 2.1204 | 2.2268 | 2.3864 | 2.5612 | 2.7284 | 2.7436
Pump Eff. | (%) | 0 | 45.018 | 62.0636 | 66.5831 | 69.482 | 65.2965 | 48.6993
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.7 | 6.03 | 6.21 | 6.44 | 6.77 | 7.04 | 7.07
Motor Input | (㎾) | 2.53 | 2.79 | 2.93 | 3.14 | 3.37 | 3.59 | 3.61
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 12 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 8.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1_MS4-4033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-2-AB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 200 | 400 | 600 | 800 | 1000
Dis. Head | (m) | 34 | 32 | 28.6 | 24.4 | 19.5 | 12.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.082711 | 0.14704 | 0.22975
Total Head | (m) | 35.7 | 33.7092 | 30.3368 | 26.1827 | 21.347 | 14.2298
Water Power | (㎾) | 0 | 1.0989 | 1.978 | 2.5607 | 2.7837 | 2.3194
Shaft Power | (㎾) | 3.0954 | 3.3418 | 3.5959 | 3.9347 | 4.1195 | 4.0117
Pump Eff. | (%) | 0 | 32.8841 | 55.0059 | 65.0791 | 67.5726 | 57.8171
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 8.15 | 8.58 | 9.01 | 9.62 | 9.94 | 9.74
Motor Input | (㎾) | 4.02 | 4.34 | 4.67 | 5.11 | 5.35 | 5.21
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 20 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin | 31 | 17
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-2-AB_MS4-5533 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 800 | 1000 | 1200 | 1330
Dis. Head | (m) | 40 | 37.2 | 32.3 | 28.7 | 25.8 | 20.8 | 13 | 6.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.14704 | 0.22975 | 0.33084 | 0.40641
Total Head | (m) | 41.7 | 38.9207 | 34.0574 | 30.4971 | 27.647 | 22.7298 | 15.0308 | 8.6064
Water Power | (㎾) | 0 | 1.9032 | 2.7757 | 3.2312 | 3.6052 | 3.7049 | 2.94 | 1.8658
Shaft Power | (㎾) | 3.7986 | 4.329 | 4.485 | 4.7814 | 5.0934 | 5.3586 | 5.2962 | 5.1246
Pump Eff. | (%) | 0 | 43.9645 | 61.8881 | 67.5778 | 70.7813 | 69.1403 | 55.5121 | 36.4084
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.22 | 11.1 | 11.39 | 11.87 | 12.46 | 12.9 | 12.79 | 12.49
Motor Input | (㎾) | 4.87 | 5.55 | 5.75 | 6.13 | 6.53 | 6.87 | 6.79 | 6.57
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-2_MS4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-3-BB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 500 | 650 | 800 | 1000 | 1100 | 1200
Dis. Head | (m) | 51 | 46.3 | 40.5 | 34.5 | 30.7 | 21 | 14.8 | 8.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.057438 | 0.09707 | 0.14704 | 0.22975 | 0.278 | 0.33084
Total Head | (m) | 52.7 | 48.0207 | 42.2574 | 36.2971 | 32.547 | 22.9298 | 16.778 | 10.3308
Water Power | (㎾) | 0 | 2.3482 | 3.444 | 3.8457 | 4.2441 | 3.7375 | 3.0083 | 2.0207
Shaft Power | (㎾) | 4.4928 | 5.0388 | 5.4912 | 5.8266 | 6.0216 | 5.8578 | 5.655 | 5.3664
Pump Eff. | (%) | 0 | 46.6026 | 62.7182 | 66.002 | 70.4818 | 63.8047 | 53.1971 | 37.6549
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 11.37 | 12.34 | 13.14 | 13.74 | 14.11 | 13.81 | 13.41 | 12.9
Motor Input | (㎾) | 5.76 | 6.46 | 7.04 | 7.47 | 7.72 | 7.51 | 7.25 | 6.88
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | SUMOTO | Turbin | 31 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-3-BB_MS4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
380V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-3)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 302 | 552 | 711 | 1002 | 1312
Dis. Head | (m) | 59 | 56 | 46 | 39 | 25 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020954 | 0.070006 | 0.11614 | 0.23067 | 0.39548
Total Head | (m) | 61.5 | 58.521 | 48.57 | 41.6161 | 27.7307 | 2.8955
Water Power | (㎾) | 0 | 2.8808 | 4.3701 | 4.823 | 4.5291 | 0.61922
Shaft Power | (㎾) | 5.168 | 6.16 | 6.736 | 7.296 | 7.84 | 7.488
Pump Eff. | (%) | 0 | 46.7655 | 64.8773 | 66.105 | 57.7696 | 8.2694
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.36 | 14.96 | 16.04 | 17.01 | 17.99 | 17.33
Motor Input | (㎾) | 6.46 | 7.7 | 8.42 | 9.12 | 9.8 | 9.36
Motor Eff. | (%) | 80 | 80 | 80 | 80 | 80 | 80
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80 | Maker | SUMOTO | Turbin | 16 | 17
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-3_MS6-10033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-5-C)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 402 | 766 | 936 | 1157 | 1246 | 1332
Dis. Head | (m) | 92 | 85 | 68 | 57 | 40 | 30 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.037129 | 0.13481 | 0.20128 | 0.30756 | 0.35669 | 0.40763
Total Head | (m) | 94.5 | 87.5371 | 70.6348 | 59.7013 | 42.8076 | 32.8567 | 7.9076
Water Power | (㎾) | 0 | 5.736 | 8.8193 | 9.1085 | 8.0731 | 6.6731 | 1.7169
Shaft Power | (㎾) | 8.5536 | 10.3113 | 12.0852 | 12.5469 | 12.3201 | 12.0204 | 10.9512
Pump Eff. | (%) | 0 | 55.6279 | 72.9762 | 72.5957 | 65.528 | 55.515 | 15.6775
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 21.37 | 24.26 | 27.41 | 27.88 | 27.87 | 27.34 | 25.39
Motor Input | (㎾) | 10.56 | 12.73 | 14.92 | 15.49 | 15.21 | 14.84 | 13.52
Motor Eff. | (%) | 81 | 81 | 81 | 81 | 81 | 81 | 81
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 65 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 29.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81 | Maker | SUMOTO | Turbin | 15 | 15
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-5_MS6-15033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-10)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 604 | 975 | 1203 | 1478
Dis. Head | (m) | 198 | 186 | 156 | 115 | 76 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.083817 | 0.21841 | 0.3325 | 0.50189
Total Head | (m) | 199.8 | 187.8207 | 157.8838 | 117.0184 | 78.1325 | 3.3019
Water Power | (㎾) | 0 | 9.1844 | 15.544 | 18.5972 | 15.3209 | 0.79547
Shaft Power | (㎾) | 16.762 | 20.1875 | 22.7375 | 25.483 | 24.701 | 21.301
Pump Eff. | (%) | 0 | 45.4956 | 68.3627 | 72.9787 | 62.0255 | 3.7344
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 38.08 | 43.72 | 48.22 | 53 | 51.5 | 45.55
Motor Input | (㎾) | 19.72 | 23.75 | 26.75 | 29.98 | 29.06 | 25.06
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 54.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 21
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-10_MS6-30033 |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-13)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 315 | 605 | 960 | 1211 | 1440
Dis. Head | (m) | 260 | 238 | 200 | 147 | 95 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.022797 | 0.084095 | 0.21174 | 0.33694 | 0.47641
Total Head | (m) | 263 | 241.0228 | 203.0841 | 150.2117 | 98.3369 | 4.4764
Water Power | (㎾) | 0 | 12.3753 | 20.0271 | 23.5051 | 19.411 | 1.0507
Shaft Power | (㎾) | 23.29 | 27.54 | 31.11 | 34.425 | 33.32 | 28.815
Pump Eff. | (%) | 0 | 44.9358 | 64.3752 | 68.2793 | 58.2564 | 3.6464
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 52 | 58 | 62 | 65 | 64.5 | 60
Motor Input | (㎾) | 27.4 | 32.4 | 36.6 | 40.5 | 39.2 | 33.9
Motor Eff. | (%) | 85 | 85 | 85 | 85 | 85 | 85
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 170 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85 | Maker | SUMOTO | Turbin | 7
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-13_MS6-40033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification