## Datasheet(46-1-B)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1-B_MF4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 9 | m | Discharge Piece | STS304
10 | Rated Capacity | 600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 14 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 384 | mm | Motor | 14.5 | kg
38 | Total | 767 | mm | Total | 21.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-1-B)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1-B_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 9 | m | Discharge Piece | STS304
10 | Rated Capacity | 600 | ℓ/min | Impeller | STS304
11 | Shut off Head | 14 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 729 | mm | Total | 20 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-1-A)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1-A_MF4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 17 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 560 | mm | Motor | 20 | kg
38 | Total | 943 | mm | Total | 26.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-1-A)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1-A_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 17 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 300 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1000 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 883 | mm | Total | 23.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-1_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 12 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 18 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 58 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 983 | mm | Total | 31.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-2-AB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-2-AB_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 19 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 33 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1096 | mm | Total | 34.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-2_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 38 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 1248 | mm | Total | 41 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-3-BB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-3-BB_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 30 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 50 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 609 | mm | Pump | 11.5 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 1361 | mm | Total | 43.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-3)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-3_MF6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 58 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 609 | mm | Pump | 11.5 | kg
37 | Motor | 645 | mm | Motor | 52 | kg
38 | Total | 1254 | mm | Total | 63.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-5-C)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-5-C_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 65 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 90 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 835 | mm | Pump | 16 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1546 | mm | Total | 74 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-10)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-10_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 195 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 54.7 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1400 | mm | Pump | 27.4 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 2307 | mm | Total | 103.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-13)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-13_MF6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 225 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 75 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1739 | mm | Pump | 34.3 | kg
37 | Motor | 1036 | mm | Motor | 92 | kg
38 | Total | 2775 | mm | Total | 126.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(46-17)
Submersible Motor Pump Data Sheet
1 | Model | PSS-46-17_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 240 | m | Discharge Piece | STS304
10 | Rated Capacity | 800 | ℓ/min | Impeller | STS304
11 | Shut off Head | 370 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 93.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 2191 | mm | Pump | 43.4 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 3596 | mm | Total | 179.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
| MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
| PSS-46-1-B | MF4-2012 | 383 |  |  | 384 |  |  | 767
|  | MF4-2033 |  |  |  | 346 |  |  | 729
| PSS-46-1-A | MF4-3012 | 383 |  |  | 560 |  |  | 943
|  | MF4-3033 |  |  |  | 500 |  |  | 883
| PSS-46-1 | MF4-5033 | 383 |  |  | 600 |  |  | 983
| PSS-46-2-AB | MF4-5033 | 496 |  |  | 600 |  |  | 1096
| PSS-46-2 | MF4-7533 | 496 |  |  | 752 |  |  | 1248
| PSS-46-3-BB | MF4-7533 | 609 |  |  | 752 |  |  | 1361
| PSS-46-3 | MF6-10033 | 609 |  |  | 645 |  |  | 1254
| PSS-46-4-BC | MF6-10033 | 722 |  |  | 645 |  |  | 1367
| PSS-46-5-C | MF6-15033 | 835 |  |  | 711 |  |  | 1546
| PSS-46-6 | MF6-20033 | 948 |  |  | 777 |  |  | 1725
| PSS-46-7-C | MF6-20033 | 1061 |  |  | 777 |  |  | 1838
| PSS-46-7 | MF6-25033 | 1061 |  |  | 841 |  |  | 1902
| PSS-46-8 | MF6-25033 | 1174 |  |  | 841 |  |  | 2015
| PSS-46-9 | MF6-30033 | 1287 |  |  | 907 |  |  | 2194
| PSS-46-10 | MF6-30033 | 1400 |  |  | 907 |  |  | 2307
| PSS-46-13 | MF6-40033 | 1739 |  |  | 1036 |  |  | 2775
| PSS-46-15 | MF6-50033 | 1965 |  |  | 1405 |  |  | 3370
| PSS-46-17 | MF6-50033 | 2191 |  |  | 1405 |  |  | 3596
123 | WEIGHT(kg)
| MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
| PSS-46-1-B | MF4-2012 | 6.9 |  |  | 14.5 |  |  | 21.4
|  | MF4-2033 |  |  |  | 13.1 |  |  | 20
| PSS-46-1-A | MF4-3012 | 6.9 |  |  | 20 |  |  | 26.9
|  | MF4-3033 |  |  |  | 17 |  |  | 23.9
| PSS-46-1 | MF4-5033 | 6.9 |  |  | 25 |  |  | 31.9
| PSS-46-2-AB | MF4-5033 | 9.2 |  |  | 25 |  |  | 34.2
| PSS-46-2 | MF4-7533 | 9.2 |  |  | 31.8 |  |  | 41
| PSS-46-3-BB | MF4-7533 | 11.5 |  |  | 31.8 |  |  | 43.3
| PSS-46-3 | MF6-10033 | 11.5 |  |  | 52 |  |  | 63.5
| PSS-46-4-BC | MF6-10033 | 13.7 |  |  | 52 |  |  | 65.7
| PSS-46-5-C | MF6-15033 | 16 |  |  | 58 |  |  | 74
| PSS-46-6 | MF6-20033 | 18.3 |  |  | 64 |  |  | 82.3
| PSS-46-7-C | MF6-20033 | 20.6 |  |  | 64 |  |  | 84.6
| PSS-46-7 | MF6-25033 | 20.6 |  |  | 70 |  |  | 90.6
| PSS-46-8 | MF6-25033 | 22.9 |  |  | 70 |  |  | 92.9
| PSS-46-9 | MF6-30033 | 25.1 |  |  | 76 |  |  | 101.1
| PSS-46-10 | MF6-30033 | 27.4 |  |  | 76 |  |  | 103.4
| PSS-46-13 | MF6-40033 | 34.3 |  |  | 92 |  |  | 126.3
| PSS-46-15 | MF6-50033 | 38.8 |  |  | 136 |  |  | 174.8
| PSS-46-17 | MF6-50033 | 43.4 |  |  | 136 |  |  | 179.4
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 4" (100mm)
|  |  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
145mm
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-46 Series

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | 품 명 |  |  | 재 질 |  | 수량
1 | Discharge |  |  | STS304 |  | 1
2 | Valve Cone |  |  |  |  | 1
3 | Valve Seat |  |  | NBR |  | Stages
4 | Top Diffuser |  |  | STS304 |  | 1
5 | Upper Bearing |  |  |  |  | 1
6 | Neck Ring |  |  | NBR |  | 1
7 | Bearing |  |  |  |  | 1
8 | Diffuser |  |  | STS304 |  | Stages
9 | Split Cone Nut |  |  |  |  | Stages
10 | Split Cone |  |  |  |  | Stages
11 | Impeller Ring |  |  |  |  | Stages
12 | Impeller |  |  |  |  | Stages
13 | Buttom Diffuser |  |  |  |  | 1
14 | Lower Bearing |  |  | - |  | 1
15 | Stop Ring |  |  | - |  | 1
16 | Space Washer |  |  | STS304 |  | 1
17 | Nut for Stop Ring |  |  |  |  | 1
18 | Buttom Neck Ring |  |  | NBR |  | 1
19 | Strainer |  |  | STS304 |  | 1
20 | Suction Interconnector |  |  |  |  | 1
21 | Pump Shaft |  |  | STS431 |  | 1
22 | Coupling |  |  | STS304 |  | 1
23 | Strap |  |  |  |  | 4
24 | Nut |  |  |  |  | 4
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-46 Series

## Test Report(46-1-B)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 153 | 300 | 454 | 608 | 765 | 950 | 1135
Dis. Head | (m) | 14.7 | 14 | 12.7 | 11.2 | 9.1 | 7.4 | 4.3 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0053783 | 0.020678 | 0.047356 | 0.084931 | 0.13446 | 0.20735 | 0.29597
Total Head | (m) | 15.7 | 15.0054 | 13.7207 | 12.2474 | 10.1849 | 8.5345 | 5.5074 | 1.396
Water Power | (㎾) | 0 | 0.37422 | 0.67094 | 0.90633 | 1.0094 | 1.0642 | 0.85281 | 0.25826
Shaft Power | (㎾) | 1.2267 | 1.3076 | 1.3547 | 1.4693 | 1.5704 | 1.6783 | 1.7457 | 1.6917
Pump Eff. | (%) | 0 | 28.6197 | 49.5255 | 61.6836 | 64.2737 | 63.4112 | 48.8533 | 15.266
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.54 | 3.69 | 3.8 | 4 | 4.2 | 4.45 | 4.58 | 4.45
Motor Input | (㎾) | 1.82 | 1.94 | 2.01 | 2.18 | 2.33 | 2.49 | 2.59 | 2.51
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 600 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 9 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1-B_MF4-2033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-1-A)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 200 | 401 | 603 | 803 | 1008 | 1221
Dis. Head | (m) | 18.1 | 17.1 | 15 | 12.8 | 9.9 | 6 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.036944 | 0.08354 | 0.14815 | 0.23344 | 0.34252
Total Head | (m) | 19.1 | 18.1092 | 16.0369 | 13.8835 | 11.0481 | 7.2334 | 2.3425
Water Power | (㎾) | 0 | 0.59036 | 1.0482 | 1.3646 | 1.4461 | 1.1885 | 0.46622
Shaft Power | (㎾) | 1.6009 | 1.7157 | 1.8242 | 2.0944 | 2.3009 | 2.4038 | 2.338
Pump Eff. | (%) | 0 | 34.4093 | 57.4621 | 65.1547 | 62.8485 | 49.4419 | 19.9408
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 10.96 | 11.72 | 12.42 | 14.13 | 15.46 | 16.21 | 15.76
Motor Input | (㎾) | 2.287 | 2.451 | 2.606 | 2.992 | 3.287 | 3.434 | 3.34
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | Franklin | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1-A_MF4-3012 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-1-A)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 204 | 401 | 603 | 803 | 1001 | 1236
Dis. Head | (m) | 18 | 17.2 | 15 | 12.7 | 10.1 | 6.3 | 0.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0095614 | 0.036944 | 0.08354 | 0.14815 | 0.23021 | 0.35099
Total Head | (m) | 19 | 18.2096 | 16.0369 | 13.7835 | 11.2481 | 7.5302 | 1.551
Water Power | (㎾) | 0 | 0.6055 | 1.0482 | 1.3548 | 1.4723 | 1.2287 | 0.31248
Shaft Power | (㎾) | 1.5862 | 1.7034 | 1.811 | 2.0803 | 2.278 | 2.3731 | 2.3043
Pump Eff. | (%) | 0 | 35.5476 | 57.8819 | 65.1224 | 64.6299 | 51.7732 | 13.5603
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.69 | 4.86 | 5.02 | 5.46 | 5.77 | 5.93 | 5.83
Motor Input | (㎾) | 2.167 | 2.327 | 2.474 | 2.842 | 3.112 | 3.242 | 3.148
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1-A_MF4-3033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 250 | 500 | 550 | 900 | 1151 | 1349
Dis. Head | (m) | 20 | 19 | 16 | 15 | 10.8 | 6.2 | 1.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014359 | 0.057438 | 0.0695 | 0.1861 | 0.30438 | 0.4181
Total Head | (m) | 20.5 | 19.5144 | 16.5574 | 15.5695 | 11.4861 | 7.0044 | 2.0181
Water Power | (㎾) | 0 | 0.79521 | 1.3494 | 1.3958 | 1.685 | 1.3141 | 0.44375
Shaft Power | (㎾) | 2.0064 | 2.201 | 2.3446 | 2.3878 | 2.8255 | 2.939 | 2.8626
Pump Eff. | (%) | 0 | 36.13 | 57.5557 | 58.4558 | 59.6354 | 44.7128 | 15.5019
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.87 | 7.07 | 7.22 | 7.24 | 7.91 | 8.03 | 7.97
Motor Input | (㎾) | 2.599 | 2.851 | 3.037 | 3.093 | 3.66 | 3.807 | 3.708
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 12 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-1_MF4-5033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-2-AB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 207 | 400 | 602 | 804 | 1009 | 1245
Dis. Head | (m) | 34 | 32.1 | 28.9 | 24.2 | 19.5 | 12.1 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0098446 | 0.03676 | 0.083263 | 0.14852 | 0.23391 | 0.35612
Total Head | (m) | 35 | 33.1098 | 29.9368 | 25.2833 | 20.6485 | 13.3339 | 2.8561
Water Power | (㎾) | 0 | 1.1172 | 1.9519 | 2.4809 | 2.706 | 2.193 | 0.57961
Shaft Power | (㎾) | 2.9645 | 3.2347 | 3.4894 | 3.8677 | 4.1225 | 4.0453 | 3.6786
Pump Eff. | (%) | 0 | 34.5369 | 55.9367 | 64.1449 | 65.6408 | 54.211 | 15.7563
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.8 | 8.16 | 8.56 | 9.12 | 9.53 | 9.43 | 8.81
Motor Input | (㎾) | 3.84 | 4.19 | 4.52 | 5.01 | 5.34 | 5.24 | 4.765
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 19 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-2-AB_MF4-5033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 254 | 504 | 752 | 1011 | 1252 | 1420
Dis. Head | (m) | 39.1 | 37 | 31.7 | 26 | 19.4 | 9 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014823 | 0.058361 | 0.12993 | 0.23483 | 0.36014 | 0.46327
Total Head | (m) | 40.1 | 38.0148 | 32.7584 | 27.1299 | 20.6348 | 10.3601 | 1.5633
Water Power | (㎾) | 0 | 1.5739 | 2.6912 | 3.3255 | 3.4005 | 2.1143 | 0.36183
Shaft Power | (㎾) | 3.4632 | 3.8998 | 4.144 | 4.625 | 4.9284 | 4.8322 | 4.588
Pump Eff. | (%) | 0 | 40.3582 | 64.9412 | 71.9022 | 68.9976 | 43.7535 | 7.8865
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.2 | 10.89 | 11.26 | 12.12 | 12.65 | 12.48 | 12
Motor Input | (㎾) | 4.68 | 5.27 | 5.6 | 6.25 | 6.66 | 6.53 | 6.2
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-2_MF4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-3-BB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 205 | 402 | 606 | 807 | 1002 | 1202 | 1317
Dis. Head | (m) | 51.8 | 49.2 | 44.1 | 37.8 | 31.2 | 21.5 | 8.4 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0096553 | 0.037129 | 0.084373 | 0.14963 | 0.23067 | 0.33195 | 0.3985
Total Head | (m) | 52.8 | 50.2097 | 45.1371 | 38.8844 | 32.3496 | 22.7307 | 9.7319 | 1.3985
Water Power | (㎾) | 0 | 1.6778 | 2.9577 | 3.8409 | 4.2553 | 3.7125 | 1.9067 | 0.30022
Shaft Power | (㎾) | 4.3364 | 4.7582 | 5.1652 | 5.7202 | 6.1346 | 6.0976 | 5.8016 | 5.3946
Pump Eff. | (%) | 0 | 35.2603 | 57.2612 | 67.1466 | 69.3656 | 60.8848 | 32.8658 | 5.5652
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 11.77 | 12.46 | 13.21 | 14.19 | 14.95 | 14.91 | 14.33 | 13.6
Motor Input | (㎾) | 5.86 | 6.43 | 6.98 | 7.73 | 8.29 | 8.24 | 7.84 | 7.29
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-3-BB_MF4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-3)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 302 | 552 | 711 | 1002 | 1312
Dis. Head | (m) | 59 | 56 | 46 | 39 | 25 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020954 | 0.070006 | 0.11614 | 0.23067 | 0.39548
Total Head | (m) | 61.5 | 58.521 | 48.57 | 41.6161 | 27.7307 | 2.8955
Water Power | (㎾) | 0 | 2.8808 | 4.3701 | 4.823 | 4.5291 | 0.61922
Shaft Power | (㎾) | 5.0388 | 6.006 | 6.5676 | 7.1136 | 7.644 | 7.3008
Pump Eff. | (%) | 0 | 47.9646 | 66.5408 | 67.8 | 59.2509 | 8.4815
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.36 | 14.96 | 16.04 | 17.01 | 17.99 | 17.33
Motor Input | (㎾) | 6.46 | 7.7 | 8.42 | 9.12 | 9.8 | 9.36
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | Franklin | Turbin | 16 | 17
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-3_MF6-10033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-5-C)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 402 | 766 | 936 | 1157 | 1246 | 1332
Dis. Head | (m) | 92 | 85 | 68 | 57 | 40 | 30 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.037129 | 0.13481 | 0.20128 | 0.30756 | 0.35669 | 0.40763
Total Head | (m) | 94.5 | 87.5371 | 70.6348 | 59.7013 | 42.8076 | 32.8567 | 7.9076
Water Power | (㎾) | 0 | 5.736 | 8.8193 | 9.1085 | 8.0731 | 6.6731 | 1.7169
Shaft Power | (㎾) | 8.4691 | 10.2095 | 11.9658 | 12.423 | 12.1984 | 11.9017 | 10.843
Pump Eff. | (%) | 0 | 56.1828 | 73.7042 | 73.3198 | 66.1817 | 56.0688 | 15.8339
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 21.37 | 24.26 | 27.41 | 28.29 | 27.87 | 27.34 | 25.39
Motor Input | (㎾) | 10.56 | 12.73 | 14.92 | 15.49 | 15.21 | 14.84 | 13.52
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 65 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | Franklin | Turbin | 15 | 15
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-5_MF6-15033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-10)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 604 | 975 | 1203 | 1478
Dis. Head | (m) | 198 | 186 | 156 | 115 | 76 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.083817 | 0.21841 | 0.3325 | 0.50189
Total Head | (m) | 199.8 | 187.8207 | 157.8838 | 117.0184 | 78.1325 | 3.3019
Water Power | (㎾) | 0 | 9.1844 | 15.544 | 18.5972 | 15.3209 | 0.79547
Shaft Power | (㎾) | 16.2887 | 19.6175 | 22.0955 | 24.7635 | 24.0036 | 20.6996
Pump Eff. | (%) | 0 | 46.8175 | 70.3491 | 75.0991 | 63.8277 | 3.8429
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 38.08 | 43.72 | 48.22 | 53 | 51.5 | 45.55
Motor Input | (㎾) | 19.72 | 23.75 | 26.75 | 29.98 | 29.06 | 25.06
Motor Eff. | (%) | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 54.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.6 | Maker | FRANKLIN | Turbin | 21
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-10_MF6-30033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-13)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 315 | 605 | 960 | 1211 | 1440
Dis. Head | (m) | 260 | 238 | 200 | 147 | 95 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.022797 | 0.084095 | 0.21174 | 0.33694 | 0.47641
Total Head | (m) | 263 | 241.0228 | 203.0841 | 150.2117 | 98.3369 | 4.4764
Water Power | (㎾) | 0 | 12.3753 | 20.0271 | 23.5051 | 19.411 | 1.0507
Shaft Power | (㎾) | 22.6872 | 26.8272 | 30.3048 | 33.534 | 32.4576 | 28.0692
Pump Eff. | (%) | 0 | 46.1297 | 66.0857 | 70.0934 | 59.8042 | 3.7433
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 52 | 58 | 64 | 70 | 68 | 60
Motor Input | (㎾) | 27.4 | 32.4 | 36.6 | 40.5 | 39.2 | 33.9
Motor Eff. | (%) | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 170 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.8 | Maker | FRANKLIN | Turbin | 7
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-13_MF6-40033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(46-17)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 350 | 580 | 830 | 1000 | 1200 | 1415
Dis. Head | (m) | 375 | 345 | 295 | 245 | 195 | 128 | 20
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.028145 | 0.077289 | 0.15828 | 0.22975 | 0.33084 | 0.46002
Total Head | (m) | 376.8 | 346.8281 | 296.8773 | 246.9583 | 197.0298 | 130.1308 | 22.26
Water Power | (㎾) | 0 | 19.7865 | 28.0668 | 33.411 | 32.1158 | 25.4536 | 5.1342
Shaft Power | (㎾) | 32.7031 | 39.0878 | 40.3218 | 40.7332 | 41.136 | 38.565 | 35.994
Pump Eff. | (%) | 0 | 50.6208 | 69.6069 | 82.0239 | 78.0724 | 66.0018 | 14.2639
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 68 | 78.3 | 85 | 92.7 | 92.9 | 89.7 | 79.9
Motor Input | (㎾) | 38.16 | 45.61 | 47.05 | 47.53 | 48 | 45 | 42
Motor Eff. | (%) | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 800 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 240 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 95.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85.7 | Maker | FRANKLIN | Turbin | 21 | 21
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-46-17_MF6-50033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification